## Rev
Revision | Description / Remarks
R0.0 | Initial release from template for Project Zero
R0.1 | IO-list according single line version R1.5 - dd 2023-11-14
R0.2 | Re-arranged columns acc. standard. - dd. 2023-11-22 Essential IO (Internal) transferred to PMS Io-list (UMS entrance, acc. Alarm panels) dd. 2023-11-24 Update acc. comments yard - dd. 2023-11-21
R0.3 | Adjusted to latest System Overview R1.6. (ASI interface moved from AMCS KEB3 to PMS IO list KEB4) - dd 2023-12-01
R0.4 | Adjusted to the latest System Overview R1.7. Deleted KEB 3 in the main saloon. - dd. 2024-02-07 Also moved internal IO from KEB3 to KEB2 for "Bridge" silence and buzzer connection
R1.0 | Added Alewijnse AC board IO (Pump control) dd. 5-03-2023
R1.1 | Name of the list adjusted to the detailed engineering project number - dd 04-04-2024 Adjusted the IO-locations of the water sensors to CB.02 - dd 04-04-2024 Changed system numbers BUMO to the yard system numbers 05-04-2024 Added fresh water system 05-04-2024
R1.2 | Added Tijssen Monitor Switching per location. 16-04-2024
R1.3 | Final Bilge & Fifi info based on Multinlines Alewijnse 2-05-2024 Added DE and Nde Pt100 readouts of propulsion motors (16-05-2024)
R1.4 | Added internal IO
R1.5 | Added Accelleration sensors 1x MTS & 1x Crew. (3-06-2024) Hull temperature Activation output added in CB.01 (04-06-2024) Added pneumatic prseeure sensor (11-06-2024)
R1.6 | IO card rename
R1.7 | Added Grey & Black Water System (04-07-2024) Changed the 750-461 pt100 cards to 750-450#2 cards in consultancy with Wouter. Added Deck Equipment Deck Crane inputs (04-07-2024)
R1.8 | Updated project to latest release, updated IO list to work with latest release and minimize validation failures in software
R1.9 | Wago 750-450 card update
R1.10 | Added "Sideboarding platform crew (PS) Closed & Locked" for Doors & hatches system - dd 08-10-2024 Added fire detection fault input dd 11-10-2024 Added KEB1 DO61 output card dd 15-10-2024 Battery Ventilation IO added dd 15-10-2024 Watertight hinged doors IO added dd 17-10-2024 Added KEB1 DO62 output card for Locker, FP & Laz Ventilation dd 28-10-2024 Added KEB1 DI30 4-20mA input card dd 29-10-2024
R1.11 | Added IO for Fire Dampers MTS Ventilation dd.4-11-2024 Added SOS locker in and outputs for bilge & Fifi system dd. 12-11-2024 Updeted Tags formulas for validation 14-11-2024 Added Input in Prefix Device kolom for valication. 14-11-2024
R1.12 | Novec Inputs added according latest info. Dd 2024-11-29
R1.13 | Monitoren IO update according latest POD layout and KVM updates dd 9-12-2024.
R1.13_FAT | IO-list confirm the production drawings R2.0 to perform the FAT (Changes in Blue). - dd 14-01-2024
R1.14_FAT | KEB1 AI34 and KEB1 DO62 removed for FAT, added module 750-626/020-002 (earth fauld detection) Removed Alarm on KEB1 DI00.2 & KEB1 DI00.2, these are spares now. KEB1 AI30 -> needs to be changed from 750-450 to 750-455. Alarm settings Bilge Alarms changed. -> Changed to Emergency and souning on BRG location Also all alarm inputs set to alarming and Fail inputs too.
R2.0 | *** Conversion version *** KEB1 AI30 -> 750-455 Kaart moet besteld worden en in Eplan van Type wijzigen. KEB1 AI33 & AI34 delete from de PLC Train KEB1 SE1_DMX -> Deleted KEB1 DO62 750-1500 toevoegen in Eplan en bestellen KEC1_P1 Verwijderd KEC1_P2 Verwijderd KEC1_P3 Verwijderd KEC1_P4 Verwijderd KEB2 AI32 & AI33 delete from de PLC Train KEC2_P1 Verwijderd KEC2_P2 Verwijderd KEC2_P3 Verwijderd KEC2_P4 Verwijderd KEC3_P1 Verwijderd KEC3_P2 Verwijderd KEC3_P3 Verwijderd KEC3_P4 Verwijderd KEB1 DI37, DI38 & DI39 verwijderd. KEB2 DI37, DI38 & DI39 verwijderd.
R2.1 | Added Monitor Source Toggle inputs for Mission Room, Ships Office, Crew mess & Captains screens. Moved PS mouse toggle from CB2 to CB1. Moved Mouse & PS Helm Monitor controls from CB2 to CB1. Added 24Vdc alarms 14E01 from Alewijnse mutilines. Added fire flap Hood 2 Added PCS Alarms in KEB1 & KEB2 MQTT kolommen added & OPC_UA kolommen deleted.
R2.2
R2.3 | Added all cables according Alewijnse Wk11 revision and Eplan so far. Added Sea water cooling pumps.
R2.4 | PS Boarding Platform Closed and locked cable added. See mail AB dd 07-04-2025 Fire Sliding Door Galley Crew Mess added, see mail AB dd 1-04-2025 Owners Deckhouse Sliding Window added dd 11-04-2025 Added Petrol sensors 1x DI & 1x AI in Keb2 dd17-04-2025 Mqtt topics added for IO in the columns added dd 24-04-2025
R2.5 | Fresh Water system revision dd 2025-05-19
R2.6 | Power tags added as per info received dd. 2025-05-22 AB Added Butterfly valves HVAC Ventilation Supply CB.02 4xDI.
R2.7 | Underwaterlights Protocol moved from the internal list to the AMCS IO-list 20250605 Moved +CB.2 AI20.2 to +CB.1 AI25.2 according Alewijnse multilines dd 20250606 MQTT messages adjusted, the + signs removed. 13-06-2025
R2.8 | MQTT added typical for topic definition dd 17-06-2025 Added IO for 24E2 that was not yet implemented. 24-06-2025 Added WTID_TECH_ROOM_ACCESS_DOOR KEB1 DI21.2 24-06-2025 Added KEB1 AI31 4-20mA card 24-06-2025
R2.9 | Added dirty oil level sensor dd 04-07-2025 Added common alarm for navigation lights 11-07-2025 Added Crew Area Access Door Nr.19 11-07-2025 Added Aft Deckhouse Access Door Nr. 36 11-07-2025 Added Technical space supply ventilation On/Off KEB1 DO62.15 11-07-2025 Added KEB1 AI32 4-20mA card 11-07-2025 due to Seawater system inputs KEB1 AI33.4 moved to KEB1 AI31.4 dd.23/7/2025

## Project definitions
Devices | Cabinet | Systems | Locations
PHW1 | 70.51 Alarm Cabinet WH | AMCS | BRG
PHW2 | 70.52 Alarm Cabinet TS | EMS | ER
PHW3 | 70.53 Alarm Cabinet ER | BMS | TS
PHU1 |  | PCS
PHU2 |  | HEALTH
KEB1 |  | PAT
KEB2 |  | TMS
KEB3 |  | Modbus
KEB4 |  | VPS
KEB5
KEF1 |  | 0900 DOORS HATCHES
KEF2 |  | 1500 PROPULSION
BRG |  | 1500 LUBE OIL
ER |  | 1700 STEERING GEAR
TS |  | 2100 BILGE FIFI
Health |  | 2100 GENERAL SERVICE
UAP |  | 2200 UNDERWATER LIGHTS
VIRT-KFE1 |  | 2500 FRESH WATER
VIRT-KFE2 |  | 2500 GREY WATER
VIRT-PHW |  | 2700 DOMESTIC EQUIPM
TMS |  | 2800 HYDRAULIC
SoftPLC |  | 2900 PNEUMATIC
NAVLIGHTS |  | 3000 DIRTY OIL
Alarming |  | 3400 SEWAGE
PHU3 |  | 3500 VENTILATION
SystemHealthMonitor |  | 3500 FIREDAMPER
WagoPlcAdapter |  | 3800 SEAWATER
UapServer |  | 4100 COOLING WATER
MdbsSrvTst |  | 4500 CCTV
MdbsClntTst |  | 4500 DYNAMIC CONV
4500 UGRID
4500 24VDC SYSTEM
4500 AMCS
7500 WINCHES
7500 DECK CRANE
7500 PASSERELLE
7500 BOARDING LADDER

## IO-List
Rev. | Deleted | Target Type | Device | Module | Module Type | Terminal | Is Subscribe | Prefix Device | Tag | Cabinet | OPC UA |  | System | Yard Tag | Description | Parent | Redundant tag | P&ID | Cable |  |  | Mqtt |  |  |  | Modbus | [7 empty] | Range |  | Unit | Precision | Alert Code | Alert |  |  |  |  | Delay On | Acknowledge Location | Sounding Locations | Alert priority | Intended Operator Response | Category A | Group Alarm | Call GEA on Alert | Disallow Inhibit | Vdr ID | General Lock |  |  | HH Lock |  |  | H Lock |  |  | L Lock |  |  | LL Lock |  |  | Do Not Log | Log To Daily Report | Log to CDP | Workstation | Timestamp
[11 empty] | Node ID | Publish Interval | [6 empty] | ID | Type | Core No. | Device | Typical | Topic | Json Path | Slave Address | Data Type | Address | Source Type | Byte Size | Swap Words | Lower | Upper | Lower | Upper |  |  |  | HH | H | L | LL | F | [10 empty] | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level
| True | [13 empty] | ALARM CABINET - AMCS Main technical Space +CB.1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 0 |  | True | GFDEnabled | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Ground Fault Diagnostics Enabled | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.GFDEnabled
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 2 |  | True | FieldVoltageAvailable | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Voltage Available | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.FieldVoltageAvailable
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 4 |  | True | PA24V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Pre-Alarm 24V | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.PA24V | [12 empty] | 6 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 5 |  | True | MA24V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Main-Alarm 24V | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.MA24V | [12 empty] | 7 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 6 |  | True | PA0V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Pre-Alarm 0V | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.PA0V | [12 empty] | 8 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 7 |  | True | MA0V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Main-Alarm 0V | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.MA0V | [12 empty] | 9 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI00 | 750-1415 | 1 |  | True | AmcsPowerSupplyFailure | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Supply Failure | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.AmcsPowerSupplyFailure | [12 empty] | 10 |  |  |  |  | False |  | TS |  | Alarm | Check Primary (G2) supply, Secundary (G3) supply and redundancy module (G1) |  |  |  |  | 1
R1.9 |  | Bool | KEB1 | DI00 | 750-1415 | 2 |  | True | Spare_DI00_2 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 3 |  | True | UmsEntranceUnitMannedSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit Manned Switch | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsEntranceUnitMannedSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 4 |  | True | UmsEntranceUnitUnmannedSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit Unmanned Switch | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsEntranceUnitUnmannedSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 5 |  | True | UmsEntranceUnitOneManSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit One Man Switch | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsEntranceUnitOneManSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 6 |  | True | UmsEntranceUnitMoreMenSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit More Men Switch | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsEntranceUnitMoreMenSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 7 |  | True | UmsOneManTimerResetButton | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS One Man Timer Reset Button | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsOneManTimerResetButton
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 8 |  | True | Spare_DI00_8 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 1 |  | True | AlarmPanelSilenceButton | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Silence Button | [6 empty] | Mqtt1 | AP | 450000 AMCS/AP | $.AlarmPanelSilenceButton
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 2 |  | True | Spare_DI01_2 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 3 |  | True | AlarmPanelGeaCallRevokeButton | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel GEA CallRevoke Button | [6 empty] | Mqtt1 | AP | 450000 AMCS/AP | $.AlarmPanelGeaCallRevokeButton
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 4 |  | True | AlarmPanelAcknowledgeButton | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Acknowledge Button | [6 empty] | Mqtt1 | AP | 450000 AMCS/AP | $.AlarmPanelAcknowledgeButton
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 5 |  | True | Spare_DI01_5 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 6 |  | True | Spare_DI01_6 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 7 |  | True | Spare_DI01_7 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 8 |  | True | Spare_DI01_8 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 1 |  | True | UmsMannedLight | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Manned Light | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsMannedLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 2 |  | True | UmsTimingOnLight | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Timing On Light | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsTimingOnLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 3 |  | True | Spare_DO00_3 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 4 |  | True | UmsOneManTimerResetLight | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS One Man Timer Reset Light | [6 empty] | Mqtt1 | UMS | 450000 AMCS/UMS | $.UmsOneManTimerResetLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 5 |  | True | AlarmPanelSilenceLight | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Silence Light | [6 empty] | Mqtt1 | AP | 450000 AMCS/AP | $.AlarmPanelSilenceLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 6 |  | True | AlarmPanelGeaCallRevokeLight | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel GEA CallRevoke Light | [6 empty] | Mqtt1 | AP | 450000 AMCS/AP | $.AlarmPanelGeaCallRevokeLight
R1.9 |  | Bool | KEB1 | DO00 | 750-1515 | 7 |  | True | MachinerySpaceBuzzerHorn | DSK_SWR |  | 1000 | 450000 AMCS |  | Machinery Space Buzzer Horn | [6 empty] | Mqtt1 | BUZ | 450000 AMCS/BUZ | $.MachinerySpaceBuzzerHorn
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 8 |  | True | AlarmPanelAcknowledgeLight | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Acknowledge Light | [6 empty] | Mqtt1 | AP | 450000 AMCS/AP | $.AlarmPanelAcknowledgeLight
R1.8 |  | Bool | KEB1 | F1 | 750-610 | 1 |  | True | AmcsPlcPowerModule1InternalFuseBlown | DSK_SWR |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 1 Internal Fuse Blown | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.AmcsPlcPowerModule1InternalFuseBlown | [12 empty] | 34 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | F1 | 750-610 | 2 |  | True | AmcsPlcPowerModule1PowerFailure | DSK_SWR |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 1 Power Failure | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.AmcsPlcPowerModule1PowerFailure | [12 empty] | 35 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI20 | 750-1415 | 1 |  | True | BILGE_LEVEL_SUB_PUMP1_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001048_1 | WATER SENSOR Submersible Pump 1 41001048_1 |  |  |  | 601W0004.3 | 14x2x0,75 |  | Mqtt1 | SUBPUMP1 | 210000 BILGE FIFI/SUBPUMP1 | $.BILGE_LEVEL_SUB_PUMP1_ALARM | [12 empty] | 36 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI20 | 750-1415 | 2 |  | True | BILGE_LEVEL_SUB_PUMP2_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001048_2 | WATER SENSOR Submersible Pump 2 41001048_2 |  |  |  | 601W0004.3 |  |  | Mqtt1 | SUBPUMP2 | 210000 BILGE FIFI/SUBPUMP2 | $.BILGE_LEVEL_SUB_PUMP2_ALARM | [12 empty] | 37 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI20 | 750-1415 | 3 |  | True | BILGE_LEVEL_SUB_PUMP3_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001048_3 | WATER SENSOR Submersible Pump 3 41001048_3 |  |  |  | 601W0004.3 |  |  | Mqtt1 | SUBPUMP3 | 210000 BILGE FIFI/SUBPUMP3 | $.BILGE_LEVEL_SUB_PUMP3_ALARM | [12 empty] | 38 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 4 |  | True | GEN_SERV_PUMP1_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001001 | General Service Pump 1 Remote Available |  |  |  | 381W0005 | 2x2x0,75 |  | Mqtt1 | SERVPUMP1 | 210000 BILGE FIFI/SERVPUMP1 | $.GEN_SERV_PUMP1_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 5 |  | True | GEN_SERV_PUMP2_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001002 | General Service Pump 2 Remote Available |  |  |  | 381W0004 | 2x2x0,75 |  | Mqtt1 | SERVPUMP2 | 210000 BILGE FIFI/SERVPUMP2 | $.GEN_SERV_PUMP2_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 6 |  | True | GEN_SERV_PUMP2_FIELD_START | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | General Service Pump 2 Field Start |  |  |  | 381W0003 | 7x1,5 |  | Mqtt1 | SERVPUMP2 | 210000 BILGE FIFI/SERVPUMP2 | $.GEN_SERV_PUMP2_FIELD_START
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 7 |  | True | GEN_SERV_PUMP2_FIELD_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | General Service Pump 2 Field Stop | [6 empty] | Mqtt1 | SERVPUMP2 | 210000 BILGE FIFI/SERVPUMP2 | $.GEN_SERV_PUMP2_FIELD_STOP
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 8 |  | True | STRIP_PUMP_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001004 | Stripping Pump Remote Available |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 | STRPUMP | 210000 BILGE FIFI/STRPUMP | $.STRIP_PUMP_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 1 |  | True | STRIP_PUMP_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Stripping Pump Running | [6 empty] | Mqtt1 | STRPUMP | 210000 BILGE FIFI/STRPUMP | $.STRIP_PUMP_RUNNING
R2.8 |  | Bool | KEB1 | DI21 | 750-1415 | 2 |  | True | WTID_TECH_ROOM_ACCESS_DOOR | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | WTID Technical Room Access Door |  |  |  | 531.1W0004 | 2x2x0,75 |  | Mqtt1 | WT | 090000 DOORS HATCHES/WT | $.WTID_TECH_ROOM_ACCESS_DOOR
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 3 |  | True | CHAIN_LOCK_PUMP_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001005 | Chain Locker Pump Remote Available |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 | CHPUMP | 210000 BILGE FIFI/CHPUMP | $.CHAIN_LOCK_PUMP_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 4 |  | True | CHAIN_LOCK_PUMP_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Chain Locker Pump Running | [6 empty] | Mqtt1 | CHPUMP | 210000 BILGE FIFI/CHPUMP | $.CHAIN_LOCK_PUMP_RUNNING
R2.2 |  | Bool | KEB1 | DI21 | 750-1415 | 5 |  | True | Spare_DI21_5 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 6 |  | True | SUBMERS_PUMP1_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006-1 | Submersible Pump 1 Remote Available |  |  |  | 381W0009 | 7x2x0.75 |  | Mqtt1 | SUBPUMP1 | 210000 BILGE FIFI/SUBPUMP1 | $.SUBMERS_PUMP1_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 7 |  | True | SUBMERS_PUMP1_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Submersible Pump 1 Running | [6 empty] | Mqtt1 | SUBPUMP1 | 210000 BILGE FIFI/SUBPUMP1 | $.SUBMERS_PUMP1_RUNNING
R1.3 |  | Bool | KEB1 | DI21 | 750-1415 | 8 |  | True | Spare_DI21_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 1 |  | True | SUBMERS_PUMP2_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006-2 | Submersible Pump 2 Remote Available |  |  |  | 381W0085 | 4x2x0.75 |  | Mqtt1 | SUBPUMP2 | 210000 BILGE FIFI/SUBPUMP2 | $.SUBMERS_PUMP2_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 2 |  | True | SUBMERS_PUMP2_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Submersible Pump 2 Running | [6 empty] | Mqtt1 | SUBPUMP2 | 210000 BILGE FIFI/SUBPUMP2 | $.SUBMERS_PUMP2_RUNNING
R1.3 |  | Bool | KEB1 | DI22 | 750-1415 | 3 |  | True | Spare_DI22_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 4 |  | True | SUBMERS_PUMP3_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_3 | Submersible Pump 3 Remote Available |  |  |  | 381W0009 | 7x2x0.75 |  | Mqtt1 | SUBPUMP3 | 210000 BILGE FIFI/SUBPUMP3 | $.SUBMERS_PUMP3_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 5 |  | True | SUBMERS_PUMP3_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Submersible Pump 3 Running | [6 empty] | Mqtt1 | SUBPUMP3 | 210000 BILGE FIFI/SUBPUMP3 | $.SUBMERS_PUMP3_RUNNING
R1.3 |  | Bool | KEB1 | DI22 | 750-1415 | 6 |  | True | Spare_DI22_6 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.8 |  | Bool | KEB1 | DI22 | 750-1415 | 7 |  | True | FRESH_WATER_MAK1_ALARM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001001_1 | Fresh Water Maker 1 Common Alarm |  |  |  | 421.1W0003 | 4x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FRESH_WATER_MAK1_ALARM | [12 empty] | 58 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI22 | 750-1415 | 8 |  | True | FRESH_WATER_MAK2_ALARM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001001_2 | Fresh Water Maker 2 Common Alarm |  |  |  | 421.1W0006 | 4x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FRESH_WATER_MAK2_ALARM | [12 empty] | 59 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI23 | 750-1415 | 1 |  | True | FRESH_WATER_CHLORINE_UNIT_ALARM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001017 | Chlorine Dosing Unit Common Alarm |  |  |  | 421.1W0010 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FRESH_WATER_CHLORINE_UNIT_ALARM | [12 empty] | 60 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 2 |  | True | TRANS_PUMP_BLCK_WAT_REM_AVAIL | +CB.1 |  | 1000 | 340000 SEWAGE | 34001001 | Transfer Pump 2 Blackwater Remote Available |  |  |  | 447W0004 | 7x2x0.75 |  | Mqtt1 |  | 340000 SEWAGE/ | $.TRANS_PUMP_BLCK_WAT_REM_AVAIL
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 3 |  | True | TRANS_PUMP_BLCK_WAT_RUNNING | +CB.1 |  | 1000 | 340000 SEWAGE |  | Transfer Pump 2 Blackwater Running | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.TRANS_PUMP_BLCK_WAT_RUNNING
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 4 |  | True | TRANS_PUMP_GREY_WAT_REM_AVAIL | +CB.1 |  | 1000 | 340000 SEWAGE | 34001002 | Transfer Pump 1 Greywater Remote Available |  |  |  | 447W0007 | 7x1,5 |  | Mqtt1 |  | 340000 SEWAGE/ | $.TRANS_PUMP_GREY_WAT_REM_AVAIL
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 5 |  | True | TRANS_PUMP_GREY_WAT_RUNNING | +CB.1 |  | 1000 | 340000 SEWAGE |  | Transfer Pump 1 Greywater Running | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.TRANS_PUMP_GREY_WAT_RUNNING
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 6 |  | True | PUMP_FWD_GREY_WAT_REM_AVAIL | +CB.1 |  | 1000 | 340000 SEWAGE | 34001003 | Pump 3 Fwd Grey Water Remote Available |  |  |  | 447W0004 | 7x2x0.75 |  | Mqtt1 |  | 340000 SEWAGE/ | $.PUMP_FWD_GREY_WAT_REM_AVAIL
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 7 |  | True | PUMP_FWD_GREY_WAT_RUNNING | +CB.1 |  | 1000 | 340000 SEWAGE |  | Pump 3 Fwd Grey Water Running | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.PUMP_FWD_GREY_WAT_RUNNING
R2.5 |  | Bool | KEB1 | DI23 | 750-1415 | 8 |  | True | FRESH_WATER_CIRC_PUMP_RUNNING | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001150 | Fresh Water Circulation Pump Running |  |  |  | 421.1W0172 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FRESH_WATER_CIRC_PUMP_RUNNING
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 1 |  | True | SEW_TREAT_RELEASE | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant Release |  |  |  | 447W0024 | 7x2x0,75 |  | Mqtt1 |  | 340000 SEWAGE/ | $.SEW_TREAT_RELEASE
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 2 |  | True | SEW_TREAT_GEN_WARNING_ALARM | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant General Warning Alarm | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.SEW_TREAT_GEN_WARNING_ALARM | [12 empty] | 69 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.5 |  | Bool | KEB1 | DI24 | 750-1415 | 3 |  | True | Sewage_Treatment_Plant_General_Alarm | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant General Alarm | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.Sewage_Treatment_Plant_General_Alarm
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 4 |  | True | SEW_TREAT_DRY_RUNN_PROT | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant Dry Running Protection & Cleaning Pump |  |  |  | 447W0024 | 7x2x0,75 |  | Mqtt1 |  | 340000 SEWAGE/ | $.SEW_TREAT_DRY_RUNN_PROT
R2.2 |  | Bool | KEB1 | DI24 | 750-1415 | 5 |  | True | PASS_HATCH_CL_LOCK | +CB.1 |  | 1000 | 750000 DECK EQUIP |  | Passerelle Hatch Closed & Locked |  |  |  | 601W0005.2 | 14x2x0.75 |  | Mqtt1 |  | 750000 DECK EQUIP/ | $.PASS_HATCH_CL_LOCK
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 6 |  | True | SBL_SB_CLOSED_LOCKED | +CB.1 |  | 1000 | 750000 DECK EQUIP |  | SB Side Boarding Ladder Closed & Locked |  |  |  | 543W0002 | 4x2x0,75 |  | Mqtt1 |  | 750000 DECK EQUIP/ | $.SBL_SB_CLOSED_LOCKED
R2.2 |  | Bool | KEB1 | DI24 | 750-1415 | 7 |  | True | SBL_COMMON_ALARM | +CB.1 |  | 1000 | 750000 DECK EQUIP |  | Side Boarding Ladder Common Alarm | [6 empty] | Mqtt1 |  | 750000 DECK EQUIP/ | $.SBL_COMMON_ALARM | [12 empty] | 74 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.5 |  | Bool | KEB1 | DI24 | 750-1415 | 8 |  | True | Sewage_Treatment_Plant_On | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant On | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.Sewage_Treatment_Plant_On
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 1 |  | True | TECH_CORRIDOR_ESC_HATCH_SB | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Technical Corridor Escape Hatch SB Nr.27 |  |  |  | 535W0016 | 2x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.TECH_CORRIDOR_ESC_HATCH_SB
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 2 |  | True | TECH_ROOM_ESC_HATCH_PS | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Technical Room Escape Hatch PS Nr.31 |  |  |  | 601W0004.3 | 14x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.TECH_ROOM_ESC_HATCH_PS
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 3 |  | True | MAIN_DECKH_VENT_HATCH_SB | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch SB Nr.33 |  |  |  | 601W0004.4/535W0020? |  |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.MAIN_DECKH_VENT_HATCH_SB
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 4 |  | True | MAIN_DECKH_VENT_HATCH_PS | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch PS Nr.34 |  |  |  | 601W0004.5/535W0022? |  |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.MAIN_DECKH_VENT_HATCH_PS
R2.8 |  | Bool | KEB1 | DI25 | 750-1415 | 5 |  | True | NOVEC_PRESSURE_SWITCH1 | +CB.1 |  | 1000 | 220000 NOVEC |  | Novec Pressure Switch 1 |  |  |  | 401.2W0011 | 2x2x0.75 |  | Mqtt1 |  | 220000 NOVEC/ | $.NOVEC_PRESSURE_SWITCH1
R2.8 |  | Bool | KEB1 | DI25 | 750-1415 | 6 |  | True | NOVEC_PRESSURE_SWITCH2 | +CB.1 |  | 1000 | 220000 NOVEC |  | Novec Pressure Switch 2 | [6 empty] | Mqtt1 |  | 220000 NOVEC/ | $.NOVEC_PRESSURE_SWITCH2
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 7 |  | True | LAZA_ACCESS_HATCH_SB_FWD | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch SB Fwd Nr.37 |  |  |  | 601W0005 | 19x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.LAZA_ACCESS_HATCH_SB_FWD
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 8 |  | True | LAZA_ACCESS_HATCH_PS_FWD | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch PS Fwd Nr.38 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.LAZA_ACCESS_HATCH_PS_FWD
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 1 |  | True | LAZA_ACCESS_HATCH_SB_MID | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch SB Mid Nr.39 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.LAZA_ACCESS_HATCH_SB_MID
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 2 |  | True | LAZA_ACCESS_HATCH_PS_MID | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch PS Mid Nr.40 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.LAZA_ACCESS_HATCH_PS_MID
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 3 |  | True | LAZA_ACCESS_HATCH_SB_AFT | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch SB Aft Nr.41 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.LAZA_ACCESS_HATCH_SB_AFT
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 4 |  | True | LAZA_ACCESS_HATCH_PS_AFT | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch PS Aft Nr.42 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.LAZA_ACCESS_HATCH_PS_AFT
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 5 |  | True | AFT_DECKH_VENT_HATCH | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Aft Deckhouse Ventilation Hatch Nr.44 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.AFT_DECKH_VENT_HATCH
R2.4 |  | Bool | KEB1 | DI26 | 750-1415 | 6 |  | True | SBP_PS_CLOSED_LOCKED | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | PS Side Boarding Platform Crew Closed & Locked |  |  |  | 543W0002 | 4x3x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.SBP_PS_CLOSED_LOCKED
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 7 |  | True | VENT_SUPP_TECH_SPACE_REM_AVAIL | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Supply Technical Space Remote Available |  |  |  | 412.4W0010 | 2x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION/ | $.VENT_SUPP_TECH_SPACE_REM_AVAIL
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 8 |  | True | VENT_SUPP_TECH_SPACE_RUNNING | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Supply Technical Space Running | [6 empty] | Mqtt1 |  | 350000 VENTILATION/ | $.VENT_SUPP_TECH_SPACE_RUNNING
R2.2 |  | Bool | KEB1 | DI27 | 750-1415 | 1 |  | True | VENT_EXTR_TECH_SPACE_REM_AVAIL | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Extractor Technical Space Remote Available |  |  |  | 412.4W0009 | 2x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION/ | $.VENT_EXTR_TECH_SPACE_REM_AVAIL
R2.2 |  | Bool | KEB1 | DI27 | 750-1415 | 2 |  | True | VENT_EXTR_TECH_SPACE_RUNNING | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Extractor Technical Space Running | [6 empty] | Mqtt1 |  | 350000 VENTILATION/ | $.VENT_EXTR_TECH_SPACE_RUNNING
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 3 |  | True | BATT_VENT_AFT_PS_ON_RUN | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS On / Run |  |  |  | 412.3W0023 | 4x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION/ | $.BATT_VENT_AFT_PS_ON_RUN
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 4 |  | True | BATT_VENT_AFT_PS_ON_FAULT | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS Fault | [6 empty] | Mqtt1 |  | 350000 VENTILATION/ | $.BATT_VENT_AFT_PS_ON_FAULT | [12 empty] | 95 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 5 |  | True | BATT_VENT_AFT_PS_ON_READY | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS Ready | [6 empty] | Mqtt1 |  | 350000 VENTILATION/ | $.BATT_VENT_AFT_PS_ON_READY
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 6 |  | True | BATT_VENT_AFT_SB_ON_RUN | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB On / Run |  |  |  | 412.3W0024 | 4x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION/ | $.BATT_VENT_AFT_SB_ON_RUN
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 7 |  | True | BATT_VENT_AFT_SB_ON_FAULT | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB Fault | [6 empty] | Mqtt1 |  | 350000 VENTILATION/ | $.BATT_VENT_AFT_SB_ON_FAULT | [12 empty] | 98 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 8 |  | True | BATT_VENT_AFT_SB_ON_READY | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB Ready | [6 empty] | Mqtt1 |  | 350000 VENTILATION/ | $.BATT_VENT_AFT_SB_ON_READY
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 1 |  | True | DRAIN_VLV_Y01_POS_OVERBOARD | +CB.1 |  | 1000 | 250000 TECHWATER | 25004014_1 | Drain water Valve Y01 Position Overboard |  |  |  | ????? | 2x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.DRAIN_VLV_Y01_POS_OVERBOARD
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 2 |  | True | DRAIN_VLV_Y01_POS_TO_PURO | +CB.1 |  | 1000 | 250000 TECHWATER | 25004014_1 | Drain water Valve Y01 Position to Puro | [6 empty] | Mqtt1 |  | 250000 TECHWATER/ | $.DRAIN_VLV_Y01_POS_TO_PURO
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 3 |  | True | TECH_WATER_CHLORINE_UNIT_ALARM | +CB.1 |  | 1000 | 250000 TECHWATER | 25004035 | Chlorine Dosing Unit Common Alarm |  |  |  | 421.2W0020 | 2x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WATER_CHLORINE_UNIT_ALARM | [12 empty] | 102 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 4 |  | True | MTS_INLET_FIRE_FLAP_RELEASED | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_1 | Main Technical Space Inlet Fire Flap Released |  |  |  | 415W0007 | 4x2x0.75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.MTS_INLET_FIRE_FLAP_RELEASED | [12 empty] | 103 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 5 |  | True | MTS_INLET_FIRE_FLAP_FULLY_RESET | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_1 | Main Technical Space Inlet Fire Flap Fully Reset | [6 empty] | Mqtt1 |  | 250000 TECHWATER/ | $.MTS_INLET_FIRE_FLAP_FULLY_RESET | [12 empty] | 104 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 6 |  | True | MTS_EXHAUST_FIRE_FLAP_RELEASED | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_2 | Main Technical Space Exhaust Fire Flap Released |  |  |  | 415W0008 | 4x2x0.75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.MTS_EXHAUST_FIRE_FLAP_RELEASED | [12 empty] | 105 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 7 |  | True | MTS_EXHAUST_FIRE_FLAP_FULLY_RESET | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_2 | Main Technical Space Exhaust Fire Flap Fully Reset | [6 empty] | Mqtt1 |  | 250000 TECHWATER/ | $.MTS_EXHAUST_FIRE_FLAP_FULLY_RESET | [12 empty] | 106 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI28 | 750-1415 | 8 |  | True | HELM_PS_OUT_DISP_ON_OFF | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS Out Display On/Off |  |  |  | 58A-C131 | CAT7 |  | Mqtt1 |  | KVM SWITCHING/ | $.HELM_PS_OUT_DISP_ON_OFF
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 1 |  | True | HELM_PS_OUT_DISP_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS Out Display Toggle |  |  |  | IW0152 | CAT7 |  | Mqtt1 |  | KVM SWITCHING/ | $.HELM_PS_OUT_DISP_TOGG
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 2 |  | True | HELM_PS_IN_DISP_ON_OFF | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Display On/Off |  |  |  | 58A-C131 | CAT7 |  | Mqtt1 |  | KVM SWITCHING/ | $.HELM_PS_IN_DISP_ON_OFF
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 3 |  | True | HELM_PS_IN_DISP_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Display Toggle |  |  |  | 58A-C101 | CAT7 |  | Mqtt1 |  | KVM SWITCHING/ | $.HELM_PS_IN_DISP_TOGG
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 4 |  | True | HELM_PS_IN_DISP_AMCS | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Display AMCS Direct |  |  |  | 58A-C101 |  |  | Mqtt1 |  | KVM SWITCHING/ | $.HELM_PS_IN_DISP_AMCS
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 5 |  | True | HELM_PS_MUTE_AMCS | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS Mute AMCS |  |  |  | IW0010 | SPEC |  | Mqtt1 |  | 450000 AMCS/ | $.HELM_PS_MUTE_AMCS
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 6 |  | True | HELM_PS_BACKLIGHT_UP_DOWN | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS Backlight Up/Down |  |  |  | 58A-C131 | CAT7 |  | Mqtt1 |  | 450000 AMCS/ | $.HELM_PS_BACKLIGHT_UP_DOWN
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 7 |  | True | HELM_PS_CREW_CALL | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS Crew Call |  |  |  | IW0010 | SPEC |  | Mqtt1 |  | 450000 AMCS/ | $.HELM_PS_CREW_CALL | [12 empty] | 114 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 8 |  | True | SHIPS_OFF_DISP_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Ships Office Display Toggle |  |  |  | 58A-C49 | CAT7 |  | Mqtt1 |  | KVM SWITCHING/ | $.SHIPS_OFF_DISP_TOGG
R2.2 |  | Bool | KEB1 | DI30 | 750-1415 | 1 |  | True | DB_GEN_SERVICE_14E1_01V01_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 01V01 Failure |  |  |  | 126W0003 | 7x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_01V01_FAULT | [12 empty] | 116 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI30 | 750-1415 | 2 |  | True | DB_GEN_SERVICE_14E1_01V02_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 01V02 Failure | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_01V02_FAULT | [12 empty] | 117 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 3 |  | True | DB_GEN_SERVICE_14E1_02V01_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 02V01 Failure | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_02V01_FAULT | [12 empty] | 118 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 4 |  | True | DB_GEN_SERVICE_14E1_02V02_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 02V02 Failure | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_02V02_FAULT | [12 empty] | 119 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.3 |  | Bool | KEB1 | DI30 | 750-1415 | 5 |  | True | SEA_WATER_COOL_PMP1_RUNNING | +CB.1 |  | 1000 | 380000 SEAWATER | 38001156_1 | Sea Water Cooling Pump 1 Running |  |  |  | 373W0029 | 4x2x0,75 |  | Mqtt1 |  | 380000 SEAWATER/ | $.SEA_WATER_COOL_PMP1_RUNNING
R2.3 |  | Bool | KEB1 | DI30 | 750-1415 | 6 |  | True | SEA_WATER_COOL_PMP1_REMOTE | +CB.1 |  | 1000 | 380000 SEAWATER | 38001156_1 | Sea Water Cooling Pump 1 Remote Available | [6 empty] | Mqtt1 |  | 380000 SEAWATER/ | $.SEA_WATER_COOL_PMP1_REMOTE
R2.8 |  | Bool | KEB1 | DI30 | 750-1415 | 7 |  | True | DB_EMERGENCY_14E2_VOLT_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Voltage Failure |  |  |  | 136W0010 | 7x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERGENCY_14E2_VOLT_FAULT
R2.8 |  | Bool | KEB1 | DI30 | 750-1415 | 8 |  | True | DB_EMERGENCY_14E2_ISOLATION_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Isolation Failure | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERGENCY_14E2_ISOLATION_FAULT
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 1 |  | True | PCS_CB.10_COM_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Common Alarm |  |  |  | =16.11-W232 | 7x2x0.75 |  | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_COM_ALARM | [12 empty] | 124 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  | 1 |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 2 |  | True | PCS_CB.10_24VDC_SERV_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 24Vdc Service Failure | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_24VDC_SERV_FAIL | [12 empty] | 125 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 3 |  | True | PCS_CB.10_24VDC_EMERG_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 24Vdc Emergency Failure | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_24VDC_EMERG_FAIL | [12 empty] | 126 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 4 |  | True | PCS_CB.10_POWER_DISTR_INS | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Power Distribution Insulation | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_POWER_DISTR_INS | [12 empty] | 127 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 5 |  | True | PCS_CB.10_HYDR_PRESS_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Hydraulic Pressure Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_HYDR_PRESS_ALARM | [12 empty] | 128 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 6 |  | True | PCS_CB.10_OIL_LEV_ALARM_SEAL_TANK | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Oil level Alarm Shaft Seal Tank | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_OIL_LEV_ALARM_SEAL_TANK | [12 empty] | 129 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 7 |  | True | PCS_CB.10_GEAR_OIL_LEV_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Gear Oil Level Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_GEAR_OIL_LEV_ALARM | [12 empty] | 130 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 8 |  | True | PCS_CB.10_GEAR_OIL_TEMP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Gear Oil Temperature Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_GEAR_OIL_TEMP_ALARM | [12 empty] | 131 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 1 |  | True | PCS_CB.10_OVERSP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Overspeed Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_OVERSP_ALARM | [12 empty] | 132 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 2 |  | True | PCS_CB.10_OVERL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Overload Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_OVERL_ALARM | [12 empty] | 133 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 3 |  | True | PCS_CB.10_AZI_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Azimuth Follow Up Failure/Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_AZI_FOLL_UP_FAIL_ALARM | [12 empty] | 134 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 4 |  | True | PCS_CB.10_PITCH_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Pitch Follow Up Failure/Alarm | [6 empty] | Mqtt1 |  | 150000 PCS/ | $.PCS_CB.10_PITCH_FOLL_UP_FAIL_ALARM | [12 empty] | 135 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI32 | 750-1415 | 5 |  | True | DECK_SLIDE_WIND_DRIVE FAIL | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System Drive Failure |  |  |  | 601W0005.3 | 19x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.DECK_SLIDE_WIND_DRIVE FAIL | [12 empty] | 136 |  |  |  |  | False |  | TS |  | Alaem | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI32 | 750-1415 | 6 |  | True | DECK_SLIDE_WIND_REM_AVAIL | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System Remote Available | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.DECK_SLIDE_WIND_REM_AVAIL
R2.4 |  | Bool | KEB1 | DI32 | 750-1415 | 7 |  | True | DECK_SLIDE_WIND_DRIVE_RUNN | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System Drive Running | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.DECK_SLIDE_WIND_DRIVE_RUNN
R2.8 |  | Bool | KEB1 | DI32 | 750-1415 | 8 |  | True | DB_EMERGENCY_14E2_CONS_ALARM | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Consumers Alarms |  |  |  | 136W0010 | 7x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERGENCY_14E2_CONS_ALARM
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 1 |  | True | BILGE_FRAME68_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_1 | Water Sensor in Hull Fr.68 Alarm |  |  |  | 601W0001.2 | 7x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI/ | $.BILGE_FRAME68_ALARM | [12 empty] | 140 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 2 |  | True | BILGE_FRAME53_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_2 | Water Sensor in Hull Fr.53 Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI/ | $.BILGE_FRAME53_ALARM | [12 empty] | 141 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 3 |  | True | BILGE_BATT_COMP_5_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_10 | Water Sensor For Battery Compartment 5 | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI/ | $.BILGE_BATT_COMP_5_ALARM | [12 empty] | 142 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 4 |  | True | BILGE_BATT_COMP_6_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_11 | Water Sensor For Battery Compartment 6 | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI/ | $.BILGE_BATT_COMP_6_ALARM | [12 empty] | 143 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 5 |  | True | W_TIGHT_HATCH_RM35_SEAL_INFLATED | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Seal Inflated |  |  |  | 535.1W0016 | 4x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM35_SEAL_INFLATED
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 6 |  | True | W_TIGHT_HATCH_RM35_DOOR_OPEN | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Door Open | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM35_DOOR_OPEN | [12 empty] | 145 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 7 |  | True | W_TIGHT_HATCH_RM35_POS_PROG_SWITCH | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Position Program Switch Exit Only Active | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM35_POS_PROG_SWITCH
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 8 |  | True | W_TIGHT_HATCH_RM35_COMMON_ALARM | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Common Alarm | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM35_COMMON_ALARM | [12 empty] | 147 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 1 |  | True | W_TIGHT_HATCH_RM36_SEAL_INFLATED | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Seal Inflated |  |  |  | 535.1W0002 | 4x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM36_SEAL_INFLATED
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 2 |  | True | W_TIGHT_HATCH_RM36_DOOR_OPEN | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Door Open | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM36_DOOR_OPEN | [12 empty] | 149 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 3 |  | True | W_TIGHT_HATCH_RM36_POS_PROG_SWITCH | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Position Program Switch Exit Only Active | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM36_POS_PROG_SWITCH
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 4 |  | True | W_TIGHT_HATCH_RM36_COMMON_ALARM | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Common Alarm | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES/ | $.W_TIGHT_HATCH_RM36_COMMON_ALARM | [12 empty] | 151 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.6 |  | Bool | KEB1 | DI34 | 750-1415 | 5 |  | True | BURGLAR_ALARM_206U01 | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U01 Passarelle |  |  |  | 601W0005.2 |  |  | Mqtt1 |  | 450000 BURGLAR/ | $.BURGLAR_ALARM_206U01
R2.6 |  | Bool | KEB1 | DI34 | 750-1415 | 6 |  | True | BURGLAR_ALARM_206U02 | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U02 Aft Entrance In Owners Cockpit | [6 empty] | Mqtt1 |  | 450000 BURGLAR/ | $.BURGLAR_ALARM_206U02
R2.6 |  | Bool | KEB1 | DI34 | 750-1415 | 7 |  | True | BURGLAR_ALARM_206U03 | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U03 Main Entrance In Main Cockpit |  |  |  | 206W0015 |  |  | Mqtt1 |  | 450000 BURGLAR/ | $.BURGLAR_ALARM_206U03
R2.8 |  | Bool | KEB1 | DI34 | 750-1415 | 8 |  | True | DB_EMERGENCY_14E2_TEMP_ALARM | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Temperature Alarm |  |  |  | 136W0010 | 7x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERGENCY_14E2_TEMP_ALARM
R2.8 |  | Bool | KEB1 | DI35 | 750-1415 | 1 |  | True | DB_EMERGENCY_14E2_EM_CONS1_FAIL | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Emergency Consumer 1 Failure |  |  |  | 136W0023 | 19x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERGENCY_14E2_EM_CONS1_FAIL
R2.8 |  | Bool | KEB1 | DI35 | 750-1415 | 2 |  | True | DB_EMERGENCY_14E2_EM_CONS2_FAIL | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Emergency Consumer 2 Failure |  |  |  | 136W0024 | 19x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERGENCY_14E2_EM_CONS2_FAIL
R2.8 |  | Bool | KEB1 | DI35 | 750-1415 | 3 |  | True | DB_GMDSS_14E3_VOLT_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB GMDSS 14E3 Voltage Failure |  |  |  | 721W0010 | 4x2x0,75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GMDSS_14E3_VOLT_FAULT
R2.8 |  | Bool | KEB1 | DI35 | 750-1415 | 4 |  | True | DB_GMDSS_14E3_ISOLATION_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB GMDSS 14E3 Isolation Failure | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GMDSS_14E3_ISOLATION_FAULT
R2.8 |  | Bool | KEB1 | DI35 | 750-1415 | 5 |  | True | DB_GMDSS_14E3_CHARGER_ALARM | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB GMDSS 14E3 Charger Alarm | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GMDSS_14E3_CHARGER_ALARM
R2.9 |  | Bool | KEB1 | DI35 | 750-1415 | 6 |  | True | MAIN_DECKH_ACCESS_DOOR | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Access Door Nr.35 |  |  |  | 601W0004.3 | 14x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.MAIN_DECKH_ACCESS_DOOR
R2.9 |  | Bool | KEB1 | DI35 | 750-1415 | 7 |  | True | AFT_DECKH_ACCESS_DOOR | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Aft Deckhouse Access Door Nr.36 |  |  |  | 601W0005 | 2x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.AFT_DECKH_ACCESS_DOOR
R2.9 |  | Bool | KEB1 | DI35 | 750-1415 | 8 |  | True | SEA_WATER_VACUUM_ALARM | +CB.1 |  | 1000 | 380000 SEAWATER | 38001014 | Seawater Pressure Vacuum Alarm |  |  |  | 373W0025 | 1x2x0.75 |  | Mqtt1 |  | 380000 SEAWATER/ | $.SEA_WATER_VACUUM_ALARM | [12 empty] | 163 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.9 |  | Bool | KEB1 | DI36 | 750-1415 | 1 |  | True | DB_GEN_SERVICE_14E1_ISOLATION_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 Isolation Failure | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_ISOLATION_FAULT
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 2 |  | True | DB_GEN_SERVICE_14E1_TEMP_ALARM | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 Temperature Alarm | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_TEMP_ALARM
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 3 |  | True | Spare_DI36_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 4 |  | True | Spare_DI36_4 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 5 |  | True | Spare_DI36_5 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 6 |  | True | Spare_DI36_6 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 7 |  | True | Spare_DI36_7 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 8 |  | True | Spare_DI36_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.2 |  | Float | KEB1 | AI20 | 750-455 | 1 |  | True | FLOW_LOWER_SALOON_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_30 | Flow Sensor Lower Saloon Cold Water |  |  |  | 601W0001 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_LOWER_SALOON_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB1 | AI20 | 750-455 | 2 |  | True | FLOW_DAYHEAD_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_31 | Flow Sensor Dayhead Cold Water |  |  |  | 601W0003 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_DAYHEAD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI20 | 750-455 | 3 |  | True | FLOW_GUEST_CABIN_SB_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_33 | Flow Sensor Guest Cabin SB Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_GUEST_CABIN_SB_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI20 | 750-455 | 4 |  | True | FLOW_GUEST_CABIN_SB_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_32 | Flow Sensor Guest Cabin SB Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_GUEST_CABIN_SB_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 1 |  | True | FLOW_GUEST_CABIN_PS_FWD_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_36 | Flow Sensor Guest Cabin PS Fwd Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_GUEST_CABIN_PS_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 2 |  | True | FLOW_GUEST_CABIN_PS_FWD_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_34 | Flow Sensor Guest Cabin PS Fwd Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_GUEST_CABIN_PS_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 3 |  | True | FLOW_GUEST_CABIN_PS_AFT_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_38 | Flow Sensor Guest Cabin PS Aft Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_GUEST_CABIN_PS_AFT_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 4 |  | True | FLOW_GUEST_CABIN_PS_AFT_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_35 | Flow Sensor Guest Cabin PS Aft Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_GUEST_CABIN_PS_AFT_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 1 |  | True | FLOW_MASTER_CABIN_SB_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_40 | Flow Sensor Master Cabin SB Hot Water |  |  |  | 601W0001 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MASTER_CABIN_SB_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 2 |  | True | FLOW_MASTER_CABIN_SB_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_37 | Flow Sensor Master Cabin SB Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MASTER_CABIN_SB_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 3 |  | True | FLOW_MASTER_CABIN_PS_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_42 | Flow Sensor Master Cabin PS Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MASTER_CABIN_PS_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 4 |  | True | FLOW_MASTER_CABIN_PS_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_39 | Flow Sensor Master Cabin PS Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MASTER_CABIN_PS_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 1 |  | True | FLOW_LAZARET_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_43 | Flow Sensor Lazaret Hot Water |  |  |  | 601W0025 | 10x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_LAZARET_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 2 |  | True | FLOW_LAZARET_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_41 | Flow Sensor Lazaret Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_LAZARET_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 3 |  | True | FLOW_WATER_SOFTNER_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001124 | Flow Sensor Water Softner Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_WATER_SOFTNER_COLD_WATER | [8 empty] | 0.1 | 75 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 4 |  | True | FLOW_MAIN_TECH_SPACE_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001123_1 | Flow Sensor Main Technical Space Hot Water |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MAIN_TECH_SPACE_HOT_WATER | [8 empty] | 5 | 300 | l/min
R2.2 |  | Float | KEB1 | AI24 | 750-455 | 1 |  | True | FLOW_MAIN_TECH_SPACE_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_1 | Flow Sensor Main Technical Space Cold Water |  |  |  | 601W0004.2 | 7x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MAIN_TECH_SPACE_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI24 | 750-455 | 2 |  | True | FLOW_MAIN_TECH_SPACE_FR45_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001123_2 | Flow Sensor Main Technical Space FR45 Bilge Area Cold Water |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_MAIN_TECH_SPACE_FR45_COLD_WATER | [8 empty] | 5 | 300 | l/min
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 3 |  | True | LEVEL_FRESH_WATER_TANK_1_FR_45_PS | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001019_1 | Level Sensor Fresh Water Tank 1 FR 45 PS |  |  |  | 421.1W0088 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.LEVEL_FRESH_WATER_TANK_1_FR_45_PS | [8 empty] | 4 | 20 | 4-20mA
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 4 |  | True | LEVEL_FRESH_WATER_TANK_2_FR_45_SB | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001019_2 | Level Sensor Fresh Water Tank 2 FR 45 SB |  |  |  | 421.1W0089 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.LEVEL_FRESH_WATER_TANK_2_FR_45_SB | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 1 |  | True | FLOW_DAYHEAD_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_C2 | Flow Sensor Dayhead Hot Water |  |  |  | 601W0003 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_DAYHEAD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.7 |  | Float | KEB1 | AI25 | 750-455 | 2 |  | True | BILGE_TANK_PRESS_SENSOR | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001050 | Bilge Tank Level |  |  |  | 381W0049 | 2x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI/ | $.BILGE_TANK_PRESS_SENSOR | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 3 |  | True | ACC_SENSOR_2_OUTPX | +CB.1 |  | 1000 | 450000 AMCS | 45019001_2 | Acceleration Sensor 2 Output X |  |  |  | 601W0005.2 | 14x2x0,75 |  | Mqtt1 |  | 450000 AMCS/ | $.ACC_SENSOR_2_OUTPX | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 4 |  | True | ACC_SENSOR_2_OUTPY | +CB.1 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 2 Output Y | [6 empty] | Mqtt1 |  | 450000 AMCS/ | $.ACC_SENSOR_2_OUTPY | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI26 | 750-455 | 1 |  | True | ACC_SENSOR_2_OUTPZ | +CB.1 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 2 Output Z | [6 empty] | Mqtt1 |  | 450000 AMCS/ | $.ACC_SENSOR_2_OUTPZ | [8 empty] | 4 | 20 | 4-20mA
R1.8 |  | Float | KEB1 | AI26 | 750-455 | 2 |  | True | PNEUMATIC_PRESSURE | +CB.1 |  | 1000 | 290000 PNEUMATIC | 29001019 | Pressure |  |  |  | 425W0003 | 2x2x0,75 |  | Mqtt1 |  | 290000 PNEUMATIC / | $.PNEUMATIC_PRESSURE | [8 empty] | 0 | 16 | Bar |  | 197 |  |  | 6 |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB1 | AI26 | 750-455 | 3 |  | True | LEVEL_GREY_WATER_TANK_AFT_SB | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_1 | Level Sensor Greywater Tank Aft FR 53 SB |  |  |  | 601W0001.2 | 7x2x0,75 |  | Mqtt1 |  | 340000 SEWAGE/ | $.LEVEL_GREY_WATER_TANK_AFT_SB | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI26 | 750-455 | 4 |  | True | LEVEL_BLACK_GREY_WATER_TANK_AFT_PS | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_2 | Level Sensor Black & Greywater Tank FR 48 PS |  |  |  | 601W0004.2 | 7x2x0,75 |  | Mqtt1 |  | 340000 SEWAGE/ | $.LEVEL_BLACK_GREY_WATER_TANK_AFT_PS | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI27 | 750-455 | 1 |  | True | LEVEL_SLUDGE_TANK_PS | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_3 | Level Sensor Sludge Tank FR 50 | [6 empty] | Mqtt1 |  | 340000 SEWAGE/ | $.LEVEL_SLUDGE_TANK_PS | [8 empty] | 4 | 20 | 4-20mA
R1.10 | Waiting on info | Float | KEB1 | AI27 | 750-455 | 2 |  | True | MAIN_DECKH_VENT_HATCH_SB_PERC | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch SB Nr.33 Percentage Open |  |  |  | 535W0020 | 4x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.MAIN_DECKH_VENT_HATCH_SB_PERC | [8 empty] | 0 | 100 | %
R1.10 | Waiting on info | Float | KEB1 | AI27 | 750-455 | 3 |  | True | MAIN_DECKH_VENT_HATCH_PS_PERC | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch PS Nr.34 Percentage Open |  |  |  | 535W0022 | 4x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.MAIN_DECKH_VENT_HATCH_PS_PERC | [8 empty] | 0 | 100 | %
R1.10 | Waiting on info | Float | KEB1 | AI27 | 750-455 | 4 |  | True | AFT_DECKH_VENT_HATCH_PERC | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Aft Deckhouse Ventilation Hatch Nr.44 Percentage Open |  |  |  | 601W0005 |  |  | Mqtt1 |  | 090000 DOORS HATCHES/ | $.AFT_DECKH_VENT_HATCH_PERC | [8 empty] | 0 | 100 | %
R1.10 | Waiting on info | Float | KEB1 | AI28 | 750-455 | 1 |  | True | TECH_WAT_SALINITY | +CB.1 |  | 1000 | 250000 TECHWATER |  | Salinity Sensor |  |  |  | ????? |  |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_SALINITY | [8 empty] | 4 | 20 | 4-20mA
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 2 |  | True | TECH_WAT_TANK1_LEVEL | +CB.1 |  | 1000 | 250000 TECHWATER | 25004025_1 | Level Sensor Technical Water Tank1 FR tbd SB |  |  |  | 421.2W0030 | 2x2x0.75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_TANK1_LEVEL | [8 empty] | 0 | 100 | % |  | 205 | 90 | 80 |  |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 3 |  | True | TECH_WAT_TANK2_LEVEL | +CB.1 |  | 1000 | 250000 TECHWATER | 25001025_2 | Level Sensor Technical Water Tank2 FR45 SB |  |  |  | 421.2W0031 | 2x2x0.75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_TANK2_LEVEL | [8 empty] | 0 | 100 | % |  | 206 | 90 | 80 |  |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB1 | AI28 | 750-455 | 4 |  | True | TECH_WAT_FLOW_CHARCOAL_FILTER_B01 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004037_4 | Flow Sensor Charcoal Filter B01 |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_FLOW_CHARCOAL_FILTER_B01 | [8 empty] | 0.2 | 150 | l/min
R2.2 |  | Float | KEB1 | AI29 | 750-455 | 1 |  | True | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B04 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004037_1 | Flow Sensor Reel For Deckwash B04 |  |  |  | 601W0025 | 10x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_FLOW_REEL_FOR_DECKWASH_B04 | [8 empty] | 0.2 | 150 | l/min
R2.2 |  | Float | KEB1 | AI29 | 750-455 | 2 |  | True | TECH_WAT_TEMP_CHARCOAL_FILTER_B01 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004038 | Temperature Sensor Charcoal Filter B01 |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_TEMP_CHARCOAL_FILTER_B01 | [8 empty] | -40 | 150 | °C
R2.2 |  | Float | KEB1 | AI29 | 750-455 | 3 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B03 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004034_1 | Flow Sensor Adiabatic Cooling Line B03 | [6 empty] | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_FLOW_ADIABATIC_COOL_B03 | [8 empty] | 0.05 | 35 | l/min
R2.5 |  | Float | KEB1 | AI29 | 750-455 | 4 |  | True | FLOW_TECHNICAL_ROOM_ENERG_REC | +CB.1 |  |  | 250000 FRESH WATER | 25001139 | Flow Sensor Technocal Room Energy Recovery |  |  |  | 421.1W0174 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.FLOW_TECHNICAL_ROOM_ENERG_REC | [8 empty] | 0.1 | 75 | l/min
R2.9 |  | Float | KEB1 | AI30 | 750-455 | 1 |  | True | DIRTY_OIL_SLUDGE_TANK_LEVEL | +CB.1 |  |  | 300000 DIRTY OIL | 30001021 | Dirty Oil Sludge Tank FR 51 SB Level |  |  |  | 365W0004 | 2x2x0.75 |  | Mqtt1 |  | 300000 DIRTY OIL/ | $.DIRTY_OIL_SLUDGE_TANK_LEVEL | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI30 | 750-455 | 2 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B09 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004034_4 | Flow Sensor Adiabatic Cooling Line B09 |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER/ | $.TECH_WAT_FLOW_ADIABATIC_COOL_B09 | [8 empty] | 0.05 | 35 | l/min
R2.8 |  | Float | KEB1 | AI30 | 750-455 | 3 |  | True | DB_EMERG_14E2_VOLTAGE | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Voltage Measurement |  |  |  | 136W0009 | 2x2x0,75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERG_14E2_VOLTAGE | [8 empty] | 4 | 20 | 4-20mA
R2.8 |  | Float | KEB1 | AI30 | 750-455 | 4 |  | True | DB_EMERG_14E2_CURRENT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Current Measurement | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERG_14E2_CURRENT | [8 empty] | 4 | 20 | 4-20mA
R2.8 |  | Float | KEB1 | AI31 | 750-455 | 1 |  | True | DB_GMDSS_14E3_VOLTAGE | +CB.1 |  |  | 450000 24VDC SYSTEM |  | 24 Vdc DB GMDSS 14E3 Voltage Measurement |  |  |  | 721W0009 | 4x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GMDSS_14E3_VOLTAGE | [8 empty] | 4 | 20 | 4-20mA
R2.8 |  | Float | KEB1 | AI31 | 750-455 | 2 |  | True | DB_GMDSS_14E3_CURRENT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB GMDSS 14E3 Current Measurement | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GMDSS_14E3_CURRENT | [8 empty] | 4 | 20 | 4-20mA
R2.8 |  | Float | KEB1 | AI31 | 750-455 | 3 |  | True | DB_GMDSS_14E3_CURRENT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB GMDSS 14E3 Earth Fault Measurement | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GMDSS_14E3_CURRENT | [8 empty] | 4 | 20 | 4-20mA
R2.9 |  | Float | KEB1 | AI31 | 750-455 | 4 |  | True | DB_EMERG_14E2_EARTH_FAULT_MON | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB Emergency 14E2 Earth Fault Measurement |  |  |  | 136W0010 | 7x2x0.75 |  | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_EMERG_14E2_EARTH_FAULT_MON | [8 empty] | 4 | 20 | 4-20mA
R2.9 |  | Float | KEB1 | AI32 | 750-455 | 1 |  | True | SEA_WATER_FLOW_IN | +CB.1 |  |  | 380000 SEAWATER | 38001164_1 | Seawater Flow In |  |  |  | 373W0023 | 4x2x0.75 |  | Mqtt1 |  | 380000 SEAWATER/ | $.SEA_WATER_FLOW_IN | [8 empty] | 4 | 20 | 4-20mA
R2.9 |  | Float | KEB1 | AI32 | 750-455 | 2 |  | True | SEA_WATER_FLOW_OUT | +CB.1 |  | 1000 | 380000 SEAWATER | 38001164_2 | Seawater Flow Out | [6 empty] | Mqtt1 |  | 380000 SEAWATER/ | $.SEA_WATER_FLOW_OUT | [8 empty] | 4 | 20 | 4-20mA
R2.9 |  | Float | KEB1 | AI32 | 750-455 | 3 |  | True | DB_GEN_SERVICE_14E1_EARTH_FAULT_MON | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 Earth Fault Measurement | [6 empty] | Mqtt1 |  | 450000 24VDC SYSTEM/ | $.DB_GEN_SERVICE_14E1_EARTH_FAULT_MON | [8 empty] | 4 | 20 | 4-20mA
R2.9 |  | Float | KEB1 | AI32 | 750-455 | 4 |  | True | Spare_AI32_4 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1 | [18 empty] | 4 | 20 | 4-20mA
R1.9 |  | Float | KEB1 | AI33 | 750-450 | 1 |  | True | STERN_THRUST_BEARING_TEMP_DE | +CB.1 |  | 1000 | 150000 PROPULSION |  | Stern Thrust Motor Bearing Temperature DE |  |  |  | =13.11-W130 | 8x2x0,75 |  | Mqtt1 |  | 150000 PROPULSION/ | $.STERN_THRUST_BEARING_TEMP_DE | [8 empty] | 0 | 150 | °C |  | 224 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.9 |  | Float | KEB1 | AI33 | 750-450 | 2 |  | True | STERN_THRUST_BEARING_TEMP_NDE | +CB.1 |  | 1000 | 150000 PROPULSION |  | Stern Thrust Motor Bearing Temperature NDE |  |  |  | =13.11-W131 | 8x2x0,75 |  | Mqtt1 |  | 150000 PROPULSION/ | $.STERN_THRUST_BEARING_TEMP_NDE | [8 empty] | 0 | 150 | °C |  | 225 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.9 |  | Float | KEB1 | AI33 | 750-450 | 3 |  | True | Spare_AI33_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1 | [18 empty] | 4 | 20 | °C
R2.5 |  | Float | KEB1 | AI33 | 750-450 | 4 |  | True | TEMP7_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_1 | Temperature Sensor S07 For Energy Recovery System |  |  |  | 421.1W0165 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.TEMP7_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.2 |  | Float | KEB1 | AI34 | 750-450 | 1 |  | True | TEMP4_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_4 | Temperature Sensor S04 For Energy Recovery System |  |  |  | 421.1W0090 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.TEMP4_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.2 |  | Float | KEB1 | AI34 | 750-450 | 2 |  | True | TEMP5_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_5 | Temperature Sensor S05 For Energy Recovery System | [6 empty] | Mqtt1 |  | 250000 FRESH WATER/ | $.TEMP5_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.5 |  | Float | KEB1 | AI34 | 750-450 | 3 |  | True | TEMP8_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_3 | Temperature Sensor S08 For Energy Recovery System |  |  |  | 421.1W0164 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.TEMP8_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.5 |  | Float | KEB1 | AI34 | 750-450 | 4 |  | True | TEMP6_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_2 | Temperature Sensor S06 For Energy Recovery System |  |  |  | 421.1W0159.1 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER/ | $.TEMP6_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R1.8 |  | Bool | KEB1 | F2 | 750-610 | 1 |  | True | AmcsPlcPowerModule2FuseBlown | +CB.1 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 2 Fuse Blown | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.AmcsPlcPowerModule2FuseBlown | [12 empty] | 232 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | F2 | 750-610 | 2 |  | True | AmcsPlcPowerModule2PowerFailure | +CB.1 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 2 Power Failure | [6 empty] | Mqtt1 | PWR | 450000 AMCS/PWR | $.AmcsPlcPowerModule2PowerFailure | [12 empty] | 233 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB1 | AO60 | 750-555 | 1 |  | True | BATT_VENT_AFT_PS_SPEED | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS Speed |  |  |  | 412.3W0003 | 2x2x0,75 |  | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_AFT_PS_SPEED | [8 empty] | 0 | 100 | %
R2.0 |  | Float | KEB1 | AO60 | 750-555 | 2 |  | True | BATT_VENT_AFT_SB_SPEED | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB Speed |  |  |  | 412.3W0006 | 2x2x0,75 |  | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_AFT_SB_SPEED | [8 empty] | 0 | 100 | %
R2.2 |  | Float | KEB1 | AO60 | 750-555 | 3 |  | True | SEW_TREAT_LEVEL_HOLDING_TANK | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_2 | Sewage Treatment Plant Level Holding Tank (AO???) |  |  |  | 447W0025 | 4x2x0,75 |  | Mqtt1 |  | 340000 SEWAGE | $.SEW_TREAT_LEVEL_HOLDING_TANK | [10 empty] | na
R2.2 |  | Float | KEB1 | AO60 | 750-555 | 4 |  | True | SEW_TREAT_LEVEL_SLUDGE_TANK | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_3 | Sewage Treatment Plant Level Sludge Tank (AO????) | [6 empty] | Mqtt1 |  | 340000 SEWAGE | $.SEW_TREAT_LEVEL_SLUDGE_TANK | [10 empty] | na
R2.3 |  | Bool | KEB1 | DO60 | 750-1500 | 1 |  | True | VENT_EXTR_TECH_SPACE_START_STOP | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Extractor Technical Space Start Stop |  |  |  | ???? |  |  | Mqtt1 |  | 350000 VENTILATION | $.VENT_EXTR_TECH_SPACE_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 2 |  | True | STRIP_PUMP_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001004 | Stripping Pump Start/Stop |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 |  | 210000 BILGE FIFI | $.STRIP_PUMP_START_STOP
R2.3 |  | Bool | KEB1 | DO60 | 750-1500 | 3 |  | True | SEA_WATER_COOL_PMP1_START_STOP | +CB.1 |  | 1000 | 380000 SEAWATER | 38001156_1 | Sea Water Cooling Pump 1 Start/Stop |  |  |  | 373W0029 | 4x2x0,75 |  | Mqtt1 |  | 380000 SEAWATER | $.SEA_WATER_COOL_PMP1_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 4 |  | True | CHAIN_LOCK_PUMP_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001005 | Chain Locker Pump Start/Stop |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 |  | 210000 BILGE FIFI | $.CHAIN_LOCK_PUMP_START_STOP
R2.3 |  | Bool | KEB1 | DO60 | 750-1500 | 5 |  | True | GEN_SERV_PUMP1_FAULT_FDBCK | +CB.1 |  | 1000 | 210000 BILGE FIFI | [8 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.GEN_SERV_PUMP1_FAULT_FDBCK
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 6 |  | True | SUBMERS_PUMP1_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_1 | Submersible Pump 1 Start/Stop |  |  |  | 381W0009 | 7x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.SUBMERS_PUMP1_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 7 |  | True | SUBMERS_PUMP2_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_2 | Submersible Pump 2 Start/Stop |  |  |  | 381W0085 | 4x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.SUBMERS_PUMP2_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 8 |  | True | SUBMERS_PUMP3_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_3 | Submersible Pump 3 Start/Stop |  |  |  | 381W0009 | 7x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.SUBMERS_PUMP3_START_STOP
R1.0 | Not in Alewijnse drawings | Bool | KEB1 | DO60 | 750-1500 | 9 |  | True | SEPARATOR_START | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001007 | Bilge Separator Start |  |  |  | 381W0017.A |  |  | Mqtt1 |  | 210000 BILGE FIFI | $.SEPARATOR_START
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 10 |  | True | ZEROING_ACC_SENSOR_1 | +CB.1 |  | 1000 | 450000 AMCS |  | Zeroing acc Sensor 1 |  |  |  | 601W0005.2 | 14x2x20,75 |  | Mqtt1 |  | 450000 AMCS | $.ZEROING_ACC_SENSOR_1
R2.4 |  | Bool | KEB1 | DO60 | 750-1500 | 11 |  | True | DECK_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System On/Off |  |  |  | 601W0005.3 | 19x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.DECK_SLIDE_WIND_ON_OFF
R1.3 |  | Bool | KEB1 | DO60 | 750-1500 | 12 |  | True | ACTIVATE_HULL_TEMP_MEASUREMENT | +CB.1 |  | 1000 | 450000 AMCS |  | Activate Hull Temperature measurement |  |  |  | INTERNAL |  |  | Mqtt1 |  | 450000 AMCS | $.ACTIVATE_HULL_TEMP_MEASUREMENT
R1.5 |  | Bool | KEB1 | DO60 | 750-1500 | 13 |  | True | TRANS_PUMP_BLCK_WAT_START_STOP | +CB.1 |  | 1000 | 340000 SEWAGE | 34001001 | Transfer Pump 2 Blackwater Start/Stop |  |  |  | 447W0003 | 10x1,5 |  | Mqtt1 |  | 340000 SEWAGE | $.TRANS_PUMP_BLCK_WAT_START_STOP
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 14 |  | True | TRANS_PUMP_GREY_WAT_START_STOP | +CB.1 |  | 1000 | 340000 SEWAGE | 34001002 | Transfer Pump 1 Greywater Start/Stop |  |  |  | 447W0007 | 7x1,5 |  | Mqtt1 |  | 340000 SEWAGE | $.TRANS_PUMP_GREY_WAT_START_STOP
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 15 |  | True | PUMP_FWD_GREY_WAT_START_STOP | +CB.1 |  | 1000 | 340000 SEWAGE | 34001003 | Pump 3 Fwd Greywater Start/Stop |  |  |  | 447W0003 | 10x1,5 |  | Mqtt1 |  | 340000 SEWAGE | $.PUMP_FWD_GREY_WAT_START_STOP
R2.5 |  | Bool | KEB1 | DO60 | 750-1500 | 16 |  | True | FRESH_WATER_CIRC_PUMP_ON_OFF | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001150 | Fresh Water Circulation Pump On/Off |  |  |  | 421.1W0172 | 2x2x0.75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FRESH_WATER_CIRC_PUMP_ON_OFF
R2.6 |  | Bool | KEB1 | DO61 | 750-1500 | 1 |  | True | BURGLAR_ALARM_SYSTEM_ON_OFF | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar System On/Off |  |  |  | 206W0031 |  |  | Mqtt1 |  | 450000 BURGLAR | $.BURGLAR_ALARM_SYSTEM_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 2 |  | True | VENT_FP_FR10_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_1 | Ventilation Forepeak FR10 PS On/Off |  |  |  | 412.5W0003 | 10x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.VENT_FP_FR10_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 3 |  | True | VENT_FP_FR10_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_1 | Ventilation Forepeak FR10 PS Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_FP_FR10_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 4 |  | True | VENT_LOCK_FR19_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_2 | Ventilation Locker FR19 PS On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR19_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 5 |  | True | VENT_LOCK_FR19_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_2 | Ventilation Locker FR19 PS Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR19_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 6 |  | True | VENT_LOCK_FR27_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_3 | Ventilation Locker FR27 PS On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR27_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 7 |  | True | VENT_LOCK_FR27_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_3 | Ventilation Locker FR27 PS Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR27_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 8 |  | True | VENT_LOCK_FR27_SB_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_4 | Ventilation Locker FR27 SB On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR27_SB_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 9 |  | True | VENT_LOCK_FR27_SB_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_4 | Ventilation Locker FR27 SB Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR27_SB_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 10 |  | True | VENT_LOCK_FR40_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_5 | Ventilation Locker FR40 PS On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR40_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 11 |  | True | VENT_LOCK_FR40_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_5 | Ventilation Locker FR40 PS Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR40_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 12 |  | True | VENT_LOCK_FR40_SB_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_6 | Ventilation Locker FR40 SB On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR40_SB_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 13 |  | True | VENT_LOCK_FR40_SB_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_6 | Ventilation Locker FR40 SB Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR40_SB_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 14 |  | True | VENT_LOCK_FR48_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_7 | Ventilation Locker FR48 PS On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR48_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 15 |  | True | VENT_LOCK_FR48_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_7 | Ventilation Locker FR48 PS Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LOCK_FR48_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 16 |  | True | VENT_LAZ_FR73_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_8 | Ventilation Lazarette FR73 PS On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LAZ_FR73_PS_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 1 |  | True | VENT_LAZ_FR73_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_8 | Ventilation Lazarette FR73 PS Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LAZ_FR73_PS_SPEED_LOW_HIGH
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 2 |  | True | VENT_LAZ_FR73_SB_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_9 | Ventilation Lazarette FR73 SB On/Off | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LAZ_FR73_SB_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 3 |  | True | VENT_LAZ_FR73_SB_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_9 | Ventilation Lazarette FR73 SB Speed Low/High | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.VENT_LAZ_FR73_SB_SPEED_LOW_HIGH
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 4 |  | True | TECH_WAT_VALVE_COLD_AIR_FR68_Y03_OPEN_CLOSE | +CB.1 |  | 1000 | 250000 TECHWATER | 25004020_1 | Valve For Cold Air Cooling Water FR68 Y03 |  |  |  | 421.2W0021 | 2x2,5 |  | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_VALVE_COLD_AIR_FR68_Y03_OPEN_CLOSE
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 5 |  | True | TECH_WAT_VALVE_COLD_AIR_FR32_Y04_OPEN_CLOSE | +CB.1 |  | 1000 | 250000 TECHWATER | 25004020_2 | Valve For Cold Air Cooling Water FR32 Y04 |  |  |  | 421.2W0022 | 2x2,5 |  | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_VALVE_COLD_AIR_FR32_Y04_OPEN_CLOSE
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 6 |  | True | TECH_WAT_VALVE_COLD_AIR_FR32_Y05_OPEN_CLOSE | +CB.1 |  | 1000 | 250000 TECHWATER | 25004020_3 | Valve For Cold Air Cooling Water FR32 Y05 |  |  |  | 421.2W0023 | 2x2,5 |  | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_VALVE_COLD_AIR_FR32_Y05_OPEN_CLOSE
R2.1 |  | Bool | KEB1 | DO62 | 750-1500 | 7 |  | True | HELM_PS_IN_MOUSE_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Mouse Toggle |  |  |  | 25A-C136 | 2x2x0.5 |  | Mqtt1 |  | KVM SWITCHING | $.HELM_PS_IN_MOUSE_TOGG
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 8 |  | True | HELM_PS_AMCS_MUTE_FB | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS AMCS Mute Feedback |  |  |  | =70.11-W279 | 7x2x0,75 |  | Mqtt1 |  | 450000 AMCS | $.HELM_PS_AMCS_MUTE_FB
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 9 |  | True | GEN_SERVICE_PUMP2_FLD_AVAIL_FDBCK | +CB.1 |  | 1000 | 210000 GENERAL SERVICE |  | General Service Pump 2 Field Available Feedback |  |  |  | 381W0003 | 7x1,5 |  | Mqtt1 |  | 210000 GENERAL SERVICE | $.GEN_SERVICE_PUMP2_FLD_AVAIL_FDBCK
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 10 |  | True | GEN_SERVICE_PUMP2_FLD_RUN_FDBCK | +CB.1 |  | 1000 | 210000 GENERAL SERVICE |  | General Service Pump 2 Field Running Feedback |  |  |  | 381W0003 |  |  | Mqtt1 |  | 210000 GENERAL SERVICE | $.GEN_SERVICE_PUMP2_FLD_RUN_FDBCK
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 11 |  | True | GEN_SERVICE_PUMP2_FLD_FAULT_FDBCK | +CB.1 |  | 1000 | 210000 GENERAL SERVICE |  | General Service Pump 2 Field Fault Feedback |  |  |  | 381W0003 |  |  | Mqtt1 |  | 210000 GENERAL SERVICE | $.GEN_SERVICE_PUMP2_FLD_FAULT_FDBCK
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 12 |  | True | AFT_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Cockpit AFT Sliding Window1~4 System On/Off |  |  |  | 601W0002 | 19x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.AFT_SLIDE_WIND_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 13 |  | True | PS_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Cockpit PS Sliding Window5~6 System On/Off | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.PS_SLIDE_WIND_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 14 |  | True | SB_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Cockpit SB Sliding Window7~8 System On/Off | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.SB_SLIDE_WIND_ON_OFF
R2.9 |  | Bool | KEB1 | DO62 | 750-1500 | 15 |  | True | VENT_SUPP_TECH_SPACE_START_STOP | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Supply Technical Space Start Stop |  |  |  | 601W0050 | 7x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.VENT_SUPP_TECH_SPACE_START_STOP
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 16 |  | True | Spare_DO62_16 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
| True | [13 empty] | Serial Interface - KEC1 Port1
| True | [13 empty] | Serial Interface - KEC1 Port2
| True | [13 empty] | Serial Interface - KEC1 Port3
| True | [13 empty] | Serial Interface - KEC1 Port4
| True | [13 empty] | ALARM CABINET - AMCS Crew Mess +CB.2
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 0 |  | True | GFDEnabled | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Ground Fault Diagnostics Enabled | [6 empty] | Mqtt1 |  | 450000 AMCS | $.GFDEnabled
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 2 |  | True | FieldVoltageAvailable | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Voltage Available | [6 empty] | Mqtt1 |  | 450000 AMCS | $.FieldVoltageAvailable
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 4 |  | True | PA24V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Pre-Alarm 24V | [6 empty] | Mqtt1 |  | 450000 AMCS | $.PA24V | [12 empty] | 293 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 5 |  | True | MA24V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Main-Alarm 24V | [6 empty] | Mqtt1 |  | 450000 AMCS | $.MA24V | [12 empty] | 294 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 6 |  | True | PA0V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Pre-Alarm 0V | [6 empty] | Mqtt1 |  | 450000 AMCS | $.PA0V | [12 empty] | 295 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 7 |  | True | MA0V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Main-Alarm 0V | [6 empty] | Mqtt1 |  | 450000 AMCS | $.MA0V | [12 empty] | 296 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI00 | 750-1415 | 1 |  | True | AmcsPowerSupplyFailure | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Supply Failure | [6 empty] | Mqtt1 |  | 450000 AMCS | $.AmcsPowerSupplyFailure | [12 empty] | 297 |  |  |  |  | False |  | TS |  | Alarm | Check Primary (G2) supply, Secundary (G3) supply and redundancy module (G1) |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI00 | 750-1415 | 2 |  | True | Spare_DI00_2 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.9 |  | Bool | KEB2 | DI00 | 750-1415 | 3 |  | True | Spare_DI00_3 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.9 |  | Bool | KEB2 | DI00 | 750-1415 | 4 |  | True | Spare_DI00_4 | +CB.2 |  | 1000 | SPARE |  | Spare
R0.4 |  | Bool | KEB2 | DI00 | 750-1415 | 5 |  | True | BridgeBuzzersPowerSupplyFailure | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Buzzers Power Supply Failure | [6 empty] | Mqtt1 |  | 450000 AMCS | $.BridgeBuzzersPowerSupplyFailure | [12 empty] | 301 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R0.4 |  | Bool | KEB2 | DI00 | 750-1415 | 6 |  | True | BridgeAlarmPanelSilenceButton | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Alarm Panel Silence Button | [6 empty] | Mqtt1 |  | 450000 AMCS | $.BridgeAlarmPanelSilenceButton
R1.4 |  | Bool | KEB2 | DI00 | 750-1415 | 7 |  | True | OperatorBuzzersPowerSupplyFailure | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Buzzers Power Supply Failure | [6 empty] | Mqtt1 |  | 450000 AMCS | $.OperatorBuzzersPowerSupplyFailure | [12 empty] | 303 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.4 |  | Bool | KEB2 | DI00 | 750-1415 | 8 |  | True | OperatorAlarmPanelSilenceButton | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Alarm Panel Silence Button | [6 empty] | Mqtt1 |  | 450000 AMCS | $.OperatorAlarmPanelSilenceButton
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 1 |  | True | UmsCabin1Silence | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Silence | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UmsCabin1Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 2 |  | True | UmsCabin2Silence | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Silence | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UmsCabin2Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 3 |  | True | UmsCabin3Silence | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Silence | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UmsCabin3Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 4 |  | True | Spare_DI01_4 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 5 |  | True | Spare_DI01_5 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 6 |  | True | Spare_DI01_6 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 7 |  | True | Spare_DI01_7 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 8 |  | True | Spare_DI01_8 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 1 |  | True | UmsCabin1Buzzer | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Buzzer | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UmsCabin1Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 2 |  | True | UmsCabin2Buzzer | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Buzzer | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UmsCabin2Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 3 |  | True | UmsCabin3Buzzer | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Buzzer | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UmsCabin3Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 4 |  | True | BridgeAlarmPanelSilenceLight | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Alarm Panel Silence Light | [6 empty] | Mqtt1 |  | 450000 AMCS | $.BridgeAlarmPanelSilenceLight
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 5 |  | True | OperatorAlarmPanelSilenceLight | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Alarm Panel Silence Light | [6 empty] | Mqtt1 |  | 450000 AMCS | $.OperatorAlarmPanelSilenceLight
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 6 |  | True | MachinerySpaceBuzzerHorn | +CB.2 |  | 1000 | 450000 AMCS |  | Machinery Space Buzzer Horn | [6 empty] | Mqtt1 |  | 450000 AMCS | $.MachinerySpaceBuzzerHorn
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 7 |  | True | BridgeAlarmPanelBuzzer | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Alarm Panel Buzzer | [6 empty] | Mqtt1 |  | 450000 AMCS | $.BridgeAlarmPanelBuzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 8 |  | True | OperatorAlarmPanelBuzzer | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Alarm Panel Buzzer | [6 empty] | Mqtt1 |  | 450000 AMCS | $.OperatorAlarmPanelBuzzer
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 1 |  | True | UMSCabin1Duty | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Duty | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UMSCabin1Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 2 |  | True | UMSCabin1AlarmLed | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Alarm Led | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UMSCabin1AlarmLed
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 3 |  | True | UMSCabin2Duty | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Duty | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UMSCabin2Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 4 |  | True | UMSCabin2AlarmLed | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Alarm Led | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UMSCabin2AlarmLed
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 5 |  | True | UMSCabin3Duty | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Duty | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UMSCabin3Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 6 |  | True | UMSCabin3AlarmLed | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Alarm Led | [6 empty] | Mqtt1 |  | 450000 AMCS | $.UMSCabin3AlarmLed
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 7 |  | True | Spare_DO01_7 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 8 |  | True | Spare_DO01_8 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.14_FAT |  | Bool | KEB2 | F1 | 750-610 | 1 |  | True | AmcsPlcPowerModule1InternalFuseBlown | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 1 Internal Fuse Blown | [6 empty] | Mqtt1 |  | 450000 AMCS | $.AmcsPlcPowerModule1InternalFuseBlown | [12 empty] | 329 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | F1 | 750-610 | 2 |  | True | AmcsPlcPowerModule1PowerFailure | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 1 Power Failure | [6 empty] | Mqtt1 |  | 450000 AMCS | $.AmcsPlcPowerModule1PowerFailure | [12 empty] | 330 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 1 |  | True | SEA_WATER_COOL_PMP2_RUNNING | +CB.2 |  | 1000 | 380000 SEAWATER | 38001156_2 | Sea Water Cooling Pump 2 Running |  |  |  | 373W0028 | 4x2x0,75 |  | Mqtt1 |  | 380000 SEAWATER | $.SEA_WATER_COOL_PMP2_RUNNING
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 2 |  | True | SEA_WATER_COOL_PMP2_REMOTE | +CB.2 |  | 1000 | 380000 SEAWATER | 38001156_2 | Sea Water Cooling Pump 2 Remote Available | [6 empty] | Mqtt1 |  | 380000 SEAWATER | $.SEA_WATER_COOL_PMP2_REMOTE
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 3 |  | True | BILGE_FRAME48_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_3 | Water Sensor in Hull Fr.48 Alarm |  |  |  | 601W0020 | 19x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME48_ALARM | [12 empty] | 333 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 4 |  | True | BILGE_FRAME46_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_4 | Water Sensor in Hull Fr.46 Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME46_ALARM | [12 empty] | 334 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 5 |  | True | BILGE_FRAME38_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_5 | Water Sensor in Hull Fr.38 Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME38_ALARM | [12 empty] | 335 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 6 |  | True | BILGE_FRAME30_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_6 | Water Sensor in Hull Fr.30 Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME30_ALARM | [12 empty] | 336 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 7 |  | True | BILGE_FRAME15_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_7 | Water Sensor in Hull Fr.15 Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME15_ALARM | [12 empty] | 337 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 8 |  | True | BILGE_FRAME13_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_8 | Water Sensor in Hull Fr.13 Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME13_ALARM | [12 empty] | 338 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 1 |  | True | BILGE_FRAME47SB_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_9 | Water Sensor in Hull Fr.47 SB Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME47SB_ALARM | [12 empty] | 339 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB2 | DI21 | 750-1415 | 2 |  | True | FIRE_SLIDE_DOOR_GALL_CREW | +CB.2 |  |  | 090000 DOORS HATCHES |  | Fire Sliding Door Galley Crew Mess |  |  |  | 533W002 | 2x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.FIRE_SLIDE_DOOR_GALL_CREW
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 3 |  | True | Spare_DI21_3 | +CB.2 |  |  | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 4 |  | True | BILGE_FRAME38PS_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_12 | Water Sensor in Hull Fr.38 PS Alarm |  |  |  | 601W0020 | 19x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME38PS_ALARM | [12 empty] | 342 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 5 |  | True | BILGE_FRAME38SB_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_13 | Water Sensor in Hull Fr.38 SB Alarm | [6 empty] | Mqtt1 |  | 210000 BILGE FIFI | $.BILGE_FRAME38SB_ALARM | [12 empty] | 343 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 6 |  | True | BCKUP_GEN_SERV_PUMP_REM_AVAIL | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001003 | Backup General Service Pump Remote Available |  |  |  | 381W0008 | 2x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.BCKUP_GEN_SERV_PUMP_REM_AVAIL
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 7 |  | True | Spare_DI21_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 8 |  | True | Spare_DI21_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 1 |  | True | CAPT_CAB_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Captains Cabin Display Toggle |  |  |  | 58A-C60 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.CAPT_CAB_DISP_TOGG
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 2 |  | True | MISSION_RM_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Mission Room Display Toggle |  |  |  | 58A-C26 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.MISSION_RM_DISP_TOGG
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 3 |  | True | CREW_MESS_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Crew Mess Display Toggle |  |  |  | 58A-C160 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.CREW_MESS_DISP_TOGG
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 4 |  | True | Spare_DI22_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 5 |  | True | Spare_DI22_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI22 | 750-1415 | 6 |  | True | DECK_CRANE_GEN_ALARM | +CB.2 |  | 1000 | 750000 DECK EQUIP | 22AJB7/10.0 | General Alarm |  |  |  | 601W0022 | 19x2x0,75 |  | Mqtt1 |  | 750000 DECK EQUIP | $.DECK_CRANE_GEN_ALARM | [12 empty] | 352 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI22 | 750-1415 | 7 |  | True | MOB_TENDER_HATCH_CL_LOCK | +CB.2 |  | 1000 | 750000 DECK EQUIP | 22AJB7/10.1 | MOB Tender Hatch Closed & Locked | [6 empty] | Mqtt1 |  | 750000 DECK EQUIP | $.MOB_TENDER_HATCH_CL_LOCK
R2.2 |  | Bool | KEB2 | DI22 | 750-1415 | 8 |  | True | GUEST_TENDER_HATCH_CL_LOCK | +CB.2 |  | 1000 | 750000 DECK EQUIP | 22AJB7/10.2 | Guest Tender Hatch Closed & Locked | [6 empty] | Mqtt1 |  | 750000 DECK EQUIP | $.GUEST_TENDER_HATCH_CL_LOCK
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 1 |  | True | SAIL_STOR_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Sail Storage Hatch Nr.2 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.SAIL_STOR_HATCH
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 2 |  | True | FOREPEAK_ACC_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Forepeak Access Hatch Nr.3 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.FOREPEAK_ACC_HATCH
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 3 |  | True | DINGHY_STOR_ACC_FWD | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Dinghy Storage Access Fwd Nr.7A | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.DINGHY_STOR_ACC_FWD
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 4 |  | True | CRANE__HATCH_AFT | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Crane Hatch Aft Nr.7D | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.CRANE__HATCH_AFT
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 5 |  | True | FORESHIP_STOR_AREA_ACC_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Foreship Storage Area Access Hatch Nr.9 | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.FORESHIP_STOR_AREA_ACC_HATCH
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 6 |  | True | CREW_ESCAPE_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Crew Escape Hatch Nr.15 |  |  |  | 601W0029 | 19x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.CREW_ESCAPE_HATCH
R2.9 |  | Bool | KEB2 | DI23 | 750-1415 | 7 |  | True | CREW_AREA_ACCESS_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Crew Area Access Door Nr.19 |  |  |  | 535W0014 | 2x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.CREW_AREA_ACCESS_DOOR
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 8 |  | True | FIRE_DETECT_FAULT | +CB.2 |  | 1000 | 450000 FIREDETECTION |  | System Fault |  |  |  | 201W0502 | 4x2x0.75 |  | Mqtt1 |  | 450000 FIREDETECTION | $.FIRE_DETECT_FAULT | [12 empty] | 362 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.9 |  | Bool | KEB2 | DI24 | 750-1415 | 1 |  | True | NAV_LIGHTS_COMMON_ALARM | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Navigation lights common Alarm |  |  |  | 601W0031 | 10x2x0.75 |  | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NAV_LIGHTS_COMMON_ALARM | [12 empty] | 363 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 2 |  | True | BATT_VENT_FWD_PS_ON_RUN | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS On / Run |  |  |  | 412.3W0010 | 7x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_PS_ON_RUN
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 3 |  | True | BATT_VENT_FWD_PS_ON_FAULT | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS Fault | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_PS_ON_FAULT | [12 empty] | 365 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 4 |  | True | BATT_VENT_FWD_PS_ON_READY | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS Ready | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_PS_ON_READY
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 5 |  | True | BATT_VENT_FWD_SB_ON_RUN | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB On / Run |  |  |  | 412.3W0011 | 7x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_SB_ON_RUN
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 6 |  | True | BATT_VENT_FWD_SB_ON_FAULT | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB Fault | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_SB_ON_FAULT | [12 empty] | 368 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 7 |  | True | BATT_VENT_FWD_SB_ON_READY | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB Ready | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_SB_ON_READY
R2.8 |  | Bool | KEB2 | DI24 | 750-1415 | 8 |  | True | Spare_DI24_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 1 |  | True | WTID_FWD_CORRIDOR_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTID Fwd End Corridor Door |  |  |  | 531.1W0005 | 2x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTID_FWD_CORRIDOR_DOOR
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 2 |  | True | WTID_AFT_CORRIDOR_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTID Aft End corridor Door |  |  |  | 531.1W0006 | 2x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTID_AFT_CORRIDOR_DOOR
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 3 |  | True | WTSD_CLOSE_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Close Door |  |  |  | 531.2W0003 | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTSD_CLOSE_DOOR | [17 empty] | False
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 4 |  | True | WTSD_MAIN_BACKUP_PWR_FAIL | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Man/Backup Power Failure |  |  |  |  | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTSD_MAIN_BACKUP_PWR_FAIL | [12 empty] | 374 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 5 |  | True | CLOSE_ALL_HULL_VALVES | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Close All Hull Valves From SOS Locker |  |  |  | 601W0034 | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.CLOSE_ALL_HULL_VALVES
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 6 |  | True | WTSD_DOOR_OPENED | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Door Opened |  |  |  | 531.2W0003 | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTSD_DOOR_OPENED
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 7 |  | True | WTSD_DOOR_CLOSED | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Door Closed |  |  |  |  | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTSD_DOOR_CLOSED
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 8 |  | True | WTSD_LOW_AIR_PRESS | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Low Air Pressure |  |  |  |  | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.WTSD_LOW_AIR_PRESS | [12 empty] | 378 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 1 |  | True | STEER_OIL_LEVEL_TOO_LOW | +CB.2 |  | 1000 | 170000 STEERING SYSTEM |  | Oil Level Too Low |  |  |  | 311W0011 | 7x2x0,75 |  | Mqtt1 |  | 170000 STEERING SYSTEM | $.STEER_OIL_LEVEL_TOO_LOW | [12 empty] | 379 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 2 |  | True | STEER_OIL_FILTER_CLOGGED | +CB.2 |  | 1000 | 170000 STEERING SYSTEM |  | Oil Filter Clogged | [6 empty] | Mqtt1 |  | 170000 STEERING SYSTEM | $.STEER_OIL_FILTER_CLOGGED | [12 empty] | 380 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 3 |  | True | STEER_24V_MONITORING | +CB.2 |  | 1000 | 170000 STEERING SYSTEM |  | 24 Voltage Monitoring | [6 empty] | Mqtt1 |  | 170000 STEERING SYSTEM | $.STEER_24V_MONITORING | [12 empty] | 381 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 4 |  | True | STEER_FREQ_DR_POWER_FAIL | +CB.2 |  | 1000 | 170000 STEERING SYSTEM |  | Frequency Drive Power Failure | [6 empty] | Mqtt1 |  | 170000 STEERING SYSTEM | $.STEER_FREQ_DR_POWER_FAIL | [12 empty] | 382 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 5 |  | True | DRAIN_VLV_Y02_POS_OVERBOARD | +CB.2 |  | 1000 | 250000 TECHWATER | 25004014_2 | Drain water Valve Y02 Position Overboard |  |  |  | 421.2W0049 | 7x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER | $.DRAIN_VLV_Y02_POS_OVERBOARD
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 6 |  | True | DRAIN_VLV_Y02_POS_TO_PURO | +CB.2 |  | 1000 | 250000 TECHWATER | 25004014_2 | Drain water Valve Y02 Position to Puro | [6 empty] | Mqtt1 |  | 250000 TECHWATER | $.DRAIN_VLV_Y02_POS_TO_PURO
R1.12 |  | Bool | KEB2 | DI26 | 750-1415 | 7 |  | True | NOVEC_RELEASED_ALARM | +CB.2 |  | 1000 | 220000 NOVEC |  | Novec Released |  |  |  | 401.2W0004 | 2x2x0.75 |  | Mqtt1 |  | 220000 NOVEC | $.NOVEC_RELEASED_ALARM | [12 empty] | 385 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.12 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 8 |  | True | NOVEC_BREAKER_TRIPPED_ALARM | +CB.2 |  | 1000 | 220000 NOVEC |  | Novec Breaker Tripped | [6 empty] | Mqtt1 |  | 220000 NOVEC | $.NOVEC_BREAKER_TRIPPED_ALARM | [12 empty] | 386 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 1 |  | True | SOS_LOCK_SUPPLY_14E1_1_Fail | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | SOS Locker Supply 14E1 1 Fail |  |  |  | 601W0033 | 4x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.SOS_LOCK_SUPPLY_14E1_1_Fail | [12 empty] | 387 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 2 |  | True | SOS_LOCK_SUPPLY_14E1_2_Fail | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | SOS Locker Supply 14E1 2 Fail |  |  |  |  | 4x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.SOS_LOCK_SUPPLY_14E1_2_Fail | [12 empty] | 388 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 3 |  | True | SOS_LOCK_SUPPLY_14E1_3_Fail | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | SOS Locker Supply 14E1 3 Fail |  |  |  |  | 4x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.SOS_LOCK_SUPPLY_14E1_3_Fail | [12 empty] | 389 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 4 |  | True | EMERG_STOP_MTS_VENT_ACTIVE | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop MTS Ventilation Active |  |  |  |  | 4x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.EMERG_STOP_MTS_VENT_ACTIVE | [12 empty] | 390 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 5 |  | True | EMERG_STOP_ACC_VENT_ACTIVE | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Accommodation Ventilation Active |  |  |  | 601W0034 | 7x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.EMERG_STOP_ACC_VENT_ACTIVE | [12 empty] | 391 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 6 |  | True | EMERG_STOP_GAL_VENT_ACTIVE | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Galley Ventilation Active | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.EMERG_STOP_GAL_VENT_ACTIVE | [12 empty] | 392 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 7 |  | True | EMERG_STOP_HAZARDOUS_CONSUMERS | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Emergency Stop Hazardous Consumers Active | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.EMERG_STOP_HAZARDOUS_CONSUMERS | [12 empty] | 393 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.3 |  | Bool | KEB2 | DI27 | 750-1415 | 8 |  | True | STEER_FREQ_DR_FAIL | +CB.2 |  | 1000 | 170000 STEERING SYSTEM |  | Frequency Drive Power Failure |  |  |  | 311W0011 | 7x2x0,75 |  | Mqtt1 |  | 170000 STEERING SYSTEM | $.STEER_FREQ_DR_FAIL
R2.4 |  | Bool | KEB2 | DI28 | 750-1415 | 1 |  | True | GAS_DETECTION_LVL_SWITCH | +CB.2 |  | 1000 | 450000 GAS DETECTION |  | Gas Detection Level Switch Petrol Locker |  |  |  | 202W0002 | 2x2x0.75 |  | Mqtt1 |  | 450000 GAS DETECTION | $.GAS_DETECTION_LVL_SWITCH | [12 empty] | 395 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 2 |  | True | HELM_SB_OUT_DISP_ON_OFF | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB Out Display On/Off |  |  |  | 58A-C130 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.HELM_SB_OUT_DISP_ON_OFF
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 3 |  | True | HELM_SB_OUT_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB Out Display Toggle |  |  |  | 58A-C72 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.HELM_SB_OUT_DISP_TOGG
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 4 |  | True | HELM_SB_IN_DISP_ON_OFF | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB In Display On/Off |  |  |  | 58A-C130 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.HELM_SB_IN_DISP_ON_OFF
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 5 |  | True | HELM_SB_IN_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB In Display Toggle |  |  |  | 58A-C103 | CAT7 |  | Mqtt1 |  | KVM SWITCHING | $.HELM_SB_IN_DISP_TOGG
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 6 |  | True | HELM_SB_IN_DISP_AMCS | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB In Display AMCS Direct | [6 empty] | Mqtt1 |  | 450000 AMCS | $.HELM_SB_IN_DISP_AMCS
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 7 |  | True | HELM_SB_MUTE_AMCS | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB Mute AMCS |  |  |  | 601W0034 | 7x2x0,75 |  | Mqtt1 |  | 450000 AMCS | $.HELM_SB_MUTE_AMCS
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 8 |  | True | HELM_SB_BACKLIGHT_UP_DOWN | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB Backlight Up/Down |  |  |  | 58A-C130 | CAT7 |  | Mqtt1 |  | 450000 AMCS | $.HELM_SB_BACKLIGHT_UP_DOWN
R1.13 |  | Bool | KEB2 | DI29 | 750-1415 | 1 |  | True | HELM_SB_CREW_CALL | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB Crew Call |  |  |  | ????? |  |  | Mqtt1 |  | 450000 AMCS | $.HELM_SB_CREW_CALL
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 2 |  | True | Spare_DI29_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 3 |  | True | Spare_DI29_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 4 |  | True | FWD_OXICELL_FIRE_FLAP_RELEASED | +CB.2 |  | 1000 | 350000 VENTILATION | 35005031_3 | FWD Space Oxycell Fire Flap Released |  |  |  | 415W0014 | 2x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.FWD_OXICELL_FIRE_FLAP_RELEASED | [12 empty] | 406 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 5 |  | True | FWD_OXYCELL_FIRE_FLAP_FULLY_RESET | +CB.2 |  | 1000 | 350000 VENTILATION | 35005031_3 | FWD Space Oxycell Fire Fire Flap Fully Reset | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.FWD_OXYCELL_FIRE_FLAP_FULLY_RESET | [12 empty] | 407 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.13 |  | Bool | KEB2 | DI29 | 750-1415 | 6 |  | True | GALLEY_HOOD_IN_FIRE_FLAP_RELEASED | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_1 | Galley Hood In Fire Flap Released |  |  |  | 415W0010 | 4x2x0.75 |  | Mqtt1 |  | 350000 VENTILATION | $.GALLEY_HOOD_IN_FIRE_FLAP_RELEASED | [12 empty] | 408 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.13 |  | Bool | KEB2 | DI29 | 750-1415 | 7 |  | True | GALLEY_HOOD_IN_FIRE_FLAP_FULLY_RESET | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_1 | Galley Hood In Fire Fire Flap Fully Reset | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.GALLEY_HOOD_IN_FIRE_FLAP_FULLY_RESET | [12 empty] | 409 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI29 | 750-1415 | 8 |  | True | GALLEY_HOOD_OUT_FIRE_FLAP_RELEASED | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_2 | Galley Hood Out Fire Flap Released | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.GALLEY_HOOD_OUT_FIRE_FLAP_RELEASED | [12 empty] | 410 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI30 | 750-1415 | 1 |  | True | GALLEY_HOOD_OUT_FIRE_FLAP_FULLY_RESET | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_2 | Galley Hood Out Fire Fire Flap Fully Reset | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.GALLEY_HOOD_OUT_FIRE_FLAP_FULLY_RESET | [12 empty] | 411 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB2 | DI30 | 750-1415 | 2 |  | True | W_TIGHT_DOOR_RM19_SEAL_INFLATED | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Door RM-19 Seal Inflated |  |  |  | 535.1W0029 | 2x2x0,75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.W_TIGHT_DOOR_RM19_SEAL_INFLATED
R2.4 |  | Bool | KEB2 | DI30 | 750-1415 | 3 |  | True | W_TIGHT_DOOR_RM19_DOOR_OPEN | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Door RM-19 Horizontal Hatch Closed | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.W_TIGHT_DOOR_RM19_DOOR_OPEN
R2.4 |  | Bool | KEB2 | DI30 | 750-1415 | 4 |  | True | W_TIGHT_DOOR_RM19_POS_PROG_SWITCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Door RM-19 Vertical Hatch Closed | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.W_TIGHT_DOOR_RM19_POS_PROG_SWITCH
R2.6 |  | Bool | KEB2 | DI30 | 750-1415 | 5 |  | True | BURGLAR_ALARM_206U04 | +CB.2 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U04 SB Side Entrance |  |  |  | 601W0031 |  |  | Mqtt1 |  | 450000 BURGLAR | $.BURGLAR_ALARM_206U04
R2.6 |  | Bool | KEB2 | DI30 | 750-1415 | 6 |  | True | BURGLAR_ALARM_206U05 | +CB.2 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U05 PS Side Entrance | [6 empty] | Mqtt1 |  | 450000 BURGLAR | $.BURGLAR_ALARM_206U05
R2.6 |  | Bool | KEB2 | DI30 | 750-1415 | 7 |  | True | BURGLAR_ALARM_206U06 | +CB.2 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U06 Crew Entrance In Racing Cockpit | [6 empty] | Mqtt1 |  | 450000 BURGLAR | $.BURGLAR_ALARM_206U06
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 8 |  | True | Spare_DI30_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 1 |  | True | PCS_CB.11_COM_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Common Alarm |  |  |  | =16.12-W232 | 7x2x0,75 |  | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_COM_ALARM | [12 empty] | 419 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  | 1 |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 2 |  | True | PCS_CB.11_24VDC_SERV_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 24Vdc Service Failure | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_24VDC_SERV_FAIL | [12 empty] | 420 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 3 |  | True | PCS_CB.11_24VDC_EMERG_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 24Vdc Emergency Failure | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_24VDC_EMERG_FAIL | [12 empty] | 421 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 4 |  | True | PCS_CB.11_POWER_DISTR_INS | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Power Distribution Insulation | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_POWER_DISTR_INS | [12 empty] | 422 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 5 |  | True | PCS_CB.11_HYDR_PRESS_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Hydraulic Pressure Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_HYDR_PRESS_ALARM | [12 empty] | 423 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 6 |  | True | PCS_CB.11_OIL_LEV_ALARM_SEAL_TANK | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Oil level Alarm Shaft Seal Tank | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_OIL_LEV_ALARM_SEAL_TANK | [12 empty] | 424 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 7 |  | True | PCS_CB.11_GEAR_OIL_LEV_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Gear Oil Level Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_GEAR_OIL_LEV_ALARM | [12 empty] | 425 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 8 |  | True | PCS_CB.11_GEAR_OIL_TEMP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Gear Oil Temperature Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_GEAR_OIL_TEMP_ALARM | [12 empty] | 426 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 1 |  | True | PCS_CB.11_OVERSP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Overspeed Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_OVERSP_ALARM | [12 empty] | 427 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 2 |  | True | PCS_CB.11_OVERL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Overload Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_OVERL_ALARM | [12 empty] | 428 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 3 |  | True | PCS_CB.11_AZI_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Azimuth Follow Up Failure/Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_AZI_FOLL_UP_FAIL_ALARM | [12 empty] | 429 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 4 |  | True | PCS_CB.11_PITCH_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Pitch Follow Up Failure/Alarm | [6 empty] | Mqtt1 |  | 150000 PCS | $.PCS_CB.11_PITCH_FOLL_UP_FAIL_ALARM | [12 empty] | 430 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 5 |  | True | HVAC_SUPPLY_VALVE_2031_1_CLOSED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_1 | HVAC Supply Butterfly Valve 2031_1 Closed |  |  |  | 412.2W1253 | 7x2x0,75 |  | Mqtt1 |  | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_1_CLOSED
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 6 |  | True | HVAC_SUPPLY_VALVE_2031_1_OPENED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_1 | HVAC Supply Butterfly Valve 2031_1 Opened | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_1_OPENED
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 7 |  | True | HVAC_SUPPLY_VALVE_2031_2_CLOSED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_2 | HVAC Supply Butterfly Valve 2031_2 Closed |  |  |  | 412.2W1259 | 7x2x0,75 |  | Mqtt1 |  | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_2_CLOSED
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 8 |  | True | HVAC_SUPPLY_VALVE_2031_2_OPENED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_2 | HVAC Supply Butterfly Valve 2031_2 Opened | [6 empty] | Mqtt1 |  | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_2_OPENED
R2.9 |  | Bool | KEB2 | DI33 | 750-1415 | 1 |  | True |  | +CB.2 |  | 1000 | KVM SWITCHING |  | SB Helm Notrot monitor DIM button |  |  |  | TEZ_58A-C130 |  |  | Mqtt1 |  | KVM SWITCHING | $.
R2.9 |  | Bool | KEB2 | DI33 | 750-1415 | 2 |  | True |  | +CB.2 |  | 1000 | KVM SWITCHING |  | SB Helm Notrot monitor Toggle (Dubbel ?? Zie DI28.3) | [6 empty] | Mqtt1 |  | KVM SWITCHING | $.
R2.9 |  | Bool | KEB2 | DI33 | 750-1415 | 3 |  | True |  | +CB.2 |  | 1000 | KVM SWITCHING |  | SB Helm Notrot monitor On/Off (Dubbel ?? Zie DI28.2) | [6 empty] | Mqtt1 |  | KVM SWITCHING | $.
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 4 |  | True | Spare_DI33_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 5 |  | True | Spare_DI33_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 6 |  | True | Spare_DI33_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 7 |  | True | Spare_DI33_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 8 |  | True | Spare_DI33_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 1 |  | True | Spare_DI34_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 2 |  | True | Spare_DI34_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 3 |  | True | Spare_DI34_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 4 |  | True | Spare_DI34_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 5 |  | True | Spare_DI34_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 6 |  | True | Spare_DI34_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 7 |  | True | Spare_DI34_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 8 |  | True | Spare_DI34_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 1 |  | True | Spare_DI35_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 2 |  | True | Spare_DI35_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 3 |  | True | Spare_DI35_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 4 |  | True | Spare_DI35_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 5 |  | True | Spare_DI35_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 6 |  | True | Spare_DI35_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 7 |  | True | Spare_DI35_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 8 |  | True | Spare_DI35_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 1 |  | True | Spare_DI36_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 2 |  | True | Spare_DI36_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 3 |  | True | Spare_DI36_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 4 |  | True | Spare_DI36_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 5 |  | True | Spare_DI36_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 6 |  | True | Spare_DI36_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 7 |  | True | Spare_DI36_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 8 |  | True | Spare_DI36_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Float | KEB2 | AI20 | 750-455 | 1 |  | True | CHAIN_LOCK_PRESS_SENSOR | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001049_1 | Chain Locker Bilge Level |  |  |  | 381W0048 | 2x2x0,75 |  | Mqtt1 |  | 210000 BILGE FIFI | $.CHAIN_LOCK_PRESS_SENSOR | [8 empty] | 0 | 1 | bar |  | 467 |  | 1 |  |  |  | 20 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.7 |  | Float | KEB2 | AI20 | 750-455 | 2 |  | True | Spare_AI20_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [18 empty] | 0 | 1 | bar |  | 468 |  | 1 |  |  |  | 20 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 3 |  | True | FLOW_CREW_MESS_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_18 | Flow Sensor Crew Mess Hot Water |  |  |  | 421.1W0106 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_MESS_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 4 |  | True | FLOW_CREW_MESS_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_17 | Flow Sensor Crew Mess Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_MESS_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 1 |  | True | FLOW_GALLEY_1_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_20 | Flow Sensor Galley 1 Hot Water |  |  |  | 421.1W0107 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_GALLEY_1_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 2 |  | True | FLOW_GALLEY_1_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_19 | Flow Sensor Galley 1 Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_GALLEY_1_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 3 |  | True | FLOW_GALLEY_2_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_22 | Flow Sensor Galley 2 Hot Water |  |  |  | 421.1W0108 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_GALLEY_2_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 4 |  | True | FLOW_GALLEY_2_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_21 | Flow Sensor Galley 2 Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_GALLEY_2_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 1 |  | True | FLOW_OVERFL_CABIN_BATHR_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_23 | Flow Sensor Overflow Cabin Bathroom Cold Water |  |  |  | 421.1W0109 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_OVERFL_CABIN_BATHR_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 2 |  | True | FLOW_GUEST_BATHR_PS_FWD_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_25 | Flow Sensor Guest Cabin Bathroom PS Fwd Hot Water |  |  |  | 421.1W0110 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_GUEST_BATHR_PS_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 3 |  | True | FLOW_GUEST_BATHR_PS_FWD_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_24 | Flow Sensor Guest Cabin Bathroom PS Fwd Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_GUEST_BATHR_PS_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 4 |  | True | FLOW_LAUNDRY_PS_1_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_15 | Flow Sensor Laundry PS 1 Hot Water |  |  |  | 421.1W0111 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_LAUNDRY_PS_1_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 1 |  | True | FLOW_LAUNDRY_PS_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_14 | Flow Sensor Laundry PS Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_LAUNDRY_PS_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 2 |  | True | FLOW_LAUNDRY_PS_2_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_16 | Flow Sensor Laundry PS 2 Hot Water |  |  |  | 421.1W0112 | 4x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_LAUNDRY_PS_2_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI23 | 750-455 | 3 |  | True | FLOW_CAPTAINS_CABIN_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_13 | Flow Sensor Captains Cabin Hot Water |  |  |  | 601W0032 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CAPTAINS_CABIN_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI23 | 750-455 | 4 |  | True | FLOW_CAPTAINS_CABIN_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_12 | Flow Sensor Captains Cabin Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CAPTAINS_CABIN_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 1 |  | True | FLOW_CREW_CABIN_SB_AFT_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_10 | Flow Sensor Crew Cabin SB Aft Hot Water |  |  |  | 601W0021 | 10x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_AFT_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 2 |  | True | FLOW_CREW_CABIN_SB_AFT_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_11 | Flow Sensor Crew Cabin SB Aft Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_AFT_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 3 |  | True | FLOW_CREW_CABIN_SB_MID_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_9 | Flow Sensor Crew Cabin SB Mid Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_MID_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 4 |  | True | FLOW_CREW_CABIN_SB_MID_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_8 | Flow Sensor Crew Cabin SB Mid Cold Water |  |  |  | 601W0032 | 19x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_MID_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 1 |  | True | FLOW_CREW_CABIN_PS_MID_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_7 | Flow Sensor Crew Cabin PS Mid Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_MID_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 2 |  | True | FLOW_CREW_CABIN_PS_MID_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_6 | Flow Sensor Crew Cabin PS Mid Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_MID_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 3 |  | True | FLOW_CREW_CABIN_SB_FWD_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_5 | Flow Sensor Crew Cabin SB Fwd Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 4 |  | True | FLOW_CREW_CABIN_SB_FWD_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_4 | Flow Sensor Crew Cabin SB Fwd Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 1 |  | True | FLOW_CREW_CABIN_PS_FWD_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_3 | Flow Sensor Crew Cabin PS Fwd Hot Water |  |  |  | 601W0021 | 10x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 2 |  | True | FLOW_CREW_CABIN_PS_FWD_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_2 | Flow Sensor Crew Cabin PS Fwd Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 3 |  | True | FLOW_DECKHOUSE_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_28 | Flow Sensor Deckhouse Hot Water |  |  |  | 601W0023 | 14x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_DECKHOUSE_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 4 |  | True | FLOW_DECKHOUSE_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_26 | Flow Sensor Deckhouse Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_DECKHOUSE_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI27 | 750-455 | 1 |  | True | FLOW_DECK_FR48_SB_TECH_COR_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_29 | Flow Sensor Deck Douche FR48 SB Technical Corridor Hot Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_DECK_FR48_SB_TECH_COR_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI27 | 750-455 | 2 |  | True | FLOW_DECK_FR48_SB_TECH_COR_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010037_27 | Flow Sensor Deck Douche FR48 SB Technical Corridor Cold Water | [6 empty] | Mqtt1 |  | 250000 FRESH WATER | $.FLOW_DECK_FR48_SB_TECH_COR_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI27 | 750-455 | 3 |  | True | PRESS_FR_46_SYSTEM_BEH_PRES_PUMPS | +CB.2 |  | 1000 | 250000 FRESH WATER | 250010036 | Pressure Sensor FR 46 System Pressure Behind Pressure Pumps |  |  |  | 421.1W0091 | 2x2x0,75 |  | Mqtt1 |  | 250000 FRESH WATER | $.PRESS_FR_46_SYSTEM_BEH_PRES_PUMPS | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI27 | 750-455 | 4 |  | True | ACC_SENSOR_1_OUTPX | +CB.2 |  | 1000 | 450000 AMCS | 45019001_1 | Acceleration Sensor 1 Output X |  |  |  | 615.2W0003 | 14x2x0,75 |  | Mqtt1 |  | 450000 AMCS | $.ACC_SENSOR_1_OUTPX | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 1 |  | True | ACC_SENSOR_1_OUTPY | +CB.2 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 1 Output Y | [6 empty] | Mqtt1 |  | 450000 AMCS | $.ACC_SENSOR_1_OUTPY | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 2 |  | True | ACC_SENSOR_1_OUTPZ | +CB.2 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 1 Output Z | [6 empty] | Mqtt1 |  | 450000 AMCS | $.ACC_SENSOR_1_OUTPZ | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 3 |  | True | LEVEL_GREY_WATER_TANK_FWD_SB | +CB.2 |  | 1000 | 340000 SEWAGE | 34001025_4 | Level Sensor Grey Water Tank Fwd FR 33 SB |  |  |  | 601W0028 | 10x2x0,75 |  | Mqtt1 |  | 340000 SEWAGE | $.LEVEL_GREY_WATER_TANK_FWD_SB | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 4 |  | True | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B05 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004037_2 | Flow Sensor Reel For Deckwash B05 |  |  |  | 601W0021 | 2x2x0.75 |  | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_FLOW_REEL_FOR_DECKWASH_B05 | [8 empty] | 0.2 | 150 | l/min
R2.2 |  | Float | KEB2 | AI29 | 750-455 | 1 |  | True | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B06 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004037_3 | Flow Sensor Reel For Deckwash B06 | [6 empty] | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_FLOW_REEL_FOR_DECKWASH_B06 | [8 empty] | 0.2 | 150 | l/min
R2.2 |  | Float | KEB2 | AI29 | 750-455 | 2 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B07 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004034_2 | Flow Sensor Adiabatic Cooling Line B07 |  |  |  | 601W0029 | 14x2x0,75 |  | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_FLOW_ADIABATIC_COOL_B07 | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI29 | 750-455 | 3 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B08 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004034_3 | Flow Sensor Adiabatic Cooling Line B08 | [6 empty] | Mqtt1 |  | 250000 TECHWATER | $.TECH_WAT_FLOW_ADIABATIC_COOL_B08 | [8 empty] | 0.05 | 35 | l/min
R2.4 |  | Float | KEB2 | AI29 | 750-455 | 4 |  | True | GAS_DETECTION_PERCT | +CB.2 |  | 1000 | 450000 GAS DETECTION |  | Gas Detection Percentage Petrol Locker |  |  |  | 202W0002 | 2x2x0.75 |  | Mqtt1 |  | 450000 GAS DETECTION | $.GAS_DETECTION_PERCT | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI30 | 750-450 | 1 |  | True | BOW_THRUST_BEARING_TEMP_DE | +CB.2 |  | 1000 | 150000 PROPULSION |  | Fwd Thrust Motor Bearing Temperature DE |  |  |  | 13.31-W130 | 8x2x0.75 |  | Mqtt1 |  | 150000 PROPULSION | $.BOW_THRUST_BEARING_TEMP_DE | [8 empty] | 0 | 150 | °C |  | 507 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB2 | AI30 | 750-450 | 2 |  | True | BOW_THRUST_BEARING_TEMP_NDE | +CB.2 |  | 1000 | 150000 PROPULSION |  | Fwd Thrust Motor Bearing Temperature NDE | [6 empty] | Mqtt1 |  | 150000 PROPULSION | $.BOW_THRUST_BEARING_TEMP_NDE | [8 empty] | 0 | 150 | °C |  | 508 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.12 |  | Float | KEB2 | AI30 | 750-450 | 3 |  | True | CABINET_INTERNAL_TEMP | +CB.2 |  | 1000 | 450000 AMCS |  | Cabinet Internal Temperature Measurement |  |  |  | INTERNAL |  |  | Mqtt1 |  | 450000 AMCS | $.CABINET_INTERNAL_TEMP | [8 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI30 | 750-450 | 4 |  | True | Spare_AI30_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [18 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 1 |  | True | Spare_AI31_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [18 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 2 |  | True | Spare_AI31_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [18 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 3 |  | True | Spare_AI31_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [18 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 4 |  | True | Spare_AI31_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [18 empty] | 4 | 20 | °C
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 1 |  | True | AmcsPlcPowerModule2FuseBlown | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 2 Fuse Blown | [6 empty] | Mqtt1 |  | 450000 AMCS | $.AmcsPlcPowerModule2FuseBlown | [12 empty] | 515 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 2 |  | True | AmcsPlcPowerModule2PowerFailure | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 2 Power Failure | [6 empty] | Mqtt1 |  | 450000 AMCS | $.AmcsPlcPowerModule2PowerFailure | [12 empty] | 516 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB2 | AO60 | 750-555 | 1 |  | True | BATT_VENT_AFT_PS_SPEED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS Speed |  |  |  | 412.3W0010 | 7x2x0,75 |  | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_AFT_PS_SPEED | [8 empty] | 0 | 100 | %
R2.2 |  | Float | KEB2 | AO60 | 750-555 | 2 |  | True | BATT_VENT_FWD_SB_SPEED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB Speed |  |  |  | 412.3W0011 | 7x2x0,75 |  | Mqtt1 |  | 350000 VENTILATION | $.BATT_VENT_FWD_SB_SPEED | [8 empty] | 0 | 100 | %
R0.1 |  | Float | KEB2 | AO60 | 750-555 | 3 |  | True | Spare_AO60_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [20 empty] | na
R0.1 |  | Float | KEB2 | AO60 | 750-555 | 4 |  | True | Spare_AO60_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [20 empty] | na
R2.3 |  | Bool | KEB2 | DO60 | 750-1500 | 1 |  | True | Spare_DO60_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DO60 | 750-1500 | 2 |  | True | HULL_VALVES_ALL_CLOSED_GREEN | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | All Hull Valves Closed (Green Pilot Light) |  |  |  | 601W0034 | 7x2x0.75 |  | Mqtt1 |  | 090000 DOORS HATCHES | $.HULL_VALVES_ALL_CLOSED_GREEN
R2.2 |  | Bool | KEB2 | DO60 | 750-1500 | 3 |  | True | HULL_VALVES_OPEN_RED | #NAME? |  | 1000 | 090000 DOORS HATCHES |  | Not All Hull Valves Closed (Red Pilot Light) | [6 empty] | Mqtt1 |  | 090000 DOORS HATCHES | $.HULL_VALVES_OPEN_RED
R1.12 |  | Bool | KEB2 | DO60 | 750-1500 | 4 |  | True | CABINET_INTERNAL_FAN_CONTROL | +CB.2 |  | 1000 | 450000 AMCS |  | Cabinet Internal Fan Control |  |  |  | INTERNAL |  |  | Mqtt1 |  | 450000 AMCS | $.CABINET_INTERNAL_FAN_CONTROL
R2.3 |  | Bool | KEB2 | DO60 | 750-1500 | 5 |  | True | SEA_WATER_COOL_PMP2_START_STOP | +CB.2 |  | 1000 | 380000 SEAWATER | 38001156_2 | Sea Water Cooling Pump 2 Start/Stop |  |  |  | 373W0028 | 4x2x0,75 |  | Mqtt1 |  | 380000 SEAWATER | $.SEA_WATER_COOL_PMP2_START_STOP
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 6 |  | True | HELM_SB_IN_MOUSE_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB In Mouse Toggle |  |  |  | 58A-C154 | 2x2x0.5 |  | Mqtt1 |  | KVM SWITCHING | $.HELM_SB_IN_MOUSE_TOGG
R2.2 |  | Bool | KEB2 | DO60 | 750-1500 | 7 |  | True | ACC_SENSOR_ZEROING_2 | +CB.2 |  | 1000 | 450000 AMCS |  | Zeroing acc Sensor 2 |  |  |  | 601W0030 | 14x2x0.75 |  | Mqtt1 |  | 450000 AMCS | $.ACC_SENSOR_ZEROING_2
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 8 |  | True | HELM_SB_AMCS_MUTE_FB | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB AMCS Mute Feedback |  |  |  | ???? |  |  | Mqtt1 |  | 450000 AMCS | $.HELM_SB_AMCS_MUTE_FB
R2.1 |  | Bool | KEB2 | DO60 | 750-1500 | 9 |  | True | Spare_DO60_9 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DO60 | 750-1500 | 10 |  | True | Spare_DO60_10 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 11 |  | True | EMERG_STOP_ACC_VENT_ACTIVATED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Accommodation Ventilation Activated |  |  |  | ???? |  |  | Mqtt1 |  | 350000 VENTILATION | $.EMERG_STOP_ACC_VENT_ACTIVATED
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 12 |  | True | EMERG_STOP_GAL_VENT_ACTIVATED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Galley Ventilation Activated |  |  |  | ???? |  |  | Mqtt1 |  | 350000 VENTILATION | $.EMERG_STOP_GAL_VENT_ACTIVATED
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 13 |  | True | Spare_DO60_13 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 14 |  | True | Spare_DO60_14 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 15 |  | True | Spare_DO60_15 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 16 |  | True | Spare_DO60_16 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port1
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port2
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port3
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port4
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC3 Port1
R1.9 |  | Bool | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Hoistable Anchor FWD Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Hoistable_Anchor_FwdStatus | 1 | Coil | 0
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | Coil | 1
R1.9 |  | Bool | NavLights |  |  |  |  | True | Starboard_BowStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Starboard BOW Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Starboard_BowStatus | 1 | Coil | 2
R1.9 |  | Bool | NavLights |  |  |  |  | True | Portside_BowStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Portside BOW Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Portside_BowStatus | 1 | Coil | 3
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | SB Nav. Spr. (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.SB_Nav_Spr_MAINStatus | 1 | Coil | 4
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | SB Nav. Spr. (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.SB_Nav_Spr_BACKUPStatus | 1 | Coil | 5
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PS Nav. Spr. (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PS_Nav_Spr_MAINStatus | 1 | Coil | 6
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PS Nav. Spr. (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PS_Nav_Spr_BACKUPStatus | 1 | Coil | 7
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Anchor AFT (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Anchor_Aft_MAINStatus | 1 | Coil | 8
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Anchor AFT (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Anchor_Aft_BACKUPStatus | 1 | Coil | 9
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Main (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Main_MAINStatus | 1 | Coil | 10
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Main (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Main_BACKUPStatus | 1 | Coil | 11
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Mizz. (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Mizz_MAINStatus | 1 | Coil | 12
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Mizz. (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Mizz_BACKUPStatus | 1 | Coil | 13
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC SB 180° (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_SB180_MAINStatus | 1 | Coil | 14
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC SB 180° (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_SB180_BACKUPStatus | 1 | Coil | 15
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC PS 180° (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_PS180_MAINStatus | 1 | Coil | 16
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC PS180° (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_PS180_BACKUPStatus | 1 | Coil | 17
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing SB 180° (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_SB180_MAINStatus | 1 | Coil | 18
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing SB 180° (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_SB180_BACKUPStatus | 1 | Coil | 19
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing PS 180° (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_PS180_MAINStatus | 1 | Coil | 20
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing PS 180° (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_PS180_BACKUPStatus | 1 | Coil | 21
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC & Sailing (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_and_Sailing_MAINStatus | 1 | Coil | 22
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC & Sailing (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_and_Sailing_BACKUPStatus | 1 | Coil | 23
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_MAINStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Stern (MAIN) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Stern_MAINStatus | 1 | Coil | 24
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_BACKUPStatus | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Stern (BACKUP) Status | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Stern_BACKUPStatus | 1 | Coil | 25
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | Coil | 26
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | Coil | 27
R1.9 |  | Bool | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Hoistable Anchor FWD Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Hoistable_Anchor_FwdCtrl | 1 | Coil | 300
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | Coil | 301
R1.9 |  | Bool | NavLights |  |  |  |  | True | Starboard_BowCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Starboard BOW Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Starboard_BowCtrl | 1 | Coil | 302
R1.9 |  | Bool | NavLights |  |  |  |  | True | Portside_BowCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Portside BOW Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Portside_BowCtrl | 1 | Coil | 303
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | SB Nav. Spr. (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.SB_Nav_Spr_MAINCtrl | 1 | Coil | 304
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | SB Nav. Spr. (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.SB_Nav_Spr_BACKUPCtrl | 1 | Coil | 305
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PS Nav. Spr. (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PS_Nav_Spr_MAINCtrl | 1 | Coil | 306
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PS Nav. Spr. (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PS_Nav_Spr_BACKUPCtrl | 1 | Coil | 307
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Anchor AFT (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Anchor_Aft_MAINCtrl | 1 | Coil | 308
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Anchor AFT (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Anchor_Aft_BACKUPCtrl | 1 | Coil | 309
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Main (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Main_MAINCtrl | 1 | Coil | 310
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Main (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Main_BACKUPCtrl | 1 | Coil | 311
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Mizz. (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Mizz_MAINCtrl | 1 | Coil | 312
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Mizz. (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Mizz_BACKUPCtrl | 1 | Coil | 313
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC SB 180° (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_SB180_MAINCtrl | 1 | Coil | 314
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC SB 180° (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_SB180_BACKUPCtrl | 1 | Coil | 315
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC PS 180° (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_PS180_MAINCtrl | 1 | Coil | 316
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC PS 180° (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_PS180_BACKUPCtrl | 1 | Coil | 317
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing SB 180° (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_SB180_MAINCtrl | 1 | Coil | 318
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing SB 180° (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_SB180_BACKUPCtrl | 1 | Coil | 319
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing PS 180° (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_PS180_MAINCtrl | 1 | Coil | 320
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing PS 180° (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_PS180_BACKUPCtrl | 1 | Coil | 321
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC & Sailing (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_and_Sailing_MAINCtrl | 1 | Coil | 322
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC & Sailing (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_and_Sailing_BACKUPCtrl | 1 | Coil | 323
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_MAINCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Stern (MAIN) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Stern_MAINCtrl | 1 | Coil | 324
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_BACKUPCtrl | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Stern (BACKUP) Control | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Stern_BACKUPCtrl | 1 | Coil | 325
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | Coil | 326
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | Coil | 327
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerMainOn | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PowerMainOn | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PowerMainOn | 1 | Coil | 1000
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerEmergencyOn | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PowerEmergencyOn | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PowerEmergencyOn | 1 | Coil | 1001
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerLampsOn | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PowerLampsOn | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PowerLampsOn | 1 | Coil | 1002
R1.9 |  | Bool | NavLights |  |  |  |  | True | ManualOperationActive | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | ManualOperationActive | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.ManualOperationActive | 1 | Coil | 1003
R1.9 |  | Bool | NavLights |  |  |  |  | True | CommunicationError | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | CommunicationError | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.CommunicationError | 1 | Coil | 2000
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Hoistable Anchor FWD Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Hoistable_Anchor_FwdOpTime | 1 | HoldingRegister | 40000 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | HoldingRegister | 40002 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Starboard_BowOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Starboard BOW Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Starboard_BowOpTime | 1 | HoldingRegister | 40004 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Portside_BowOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Portside BOW Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Portside_BowOpTime | 1 | HoldingRegister | 40006 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | SB Nav. Spr. (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.SB_Nav_Spr_MAINOpTime | 1 | HoldingRegister | 40008 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | SB Nav. Spr. (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.SB_Nav_Spr_BACKUPOpTime | 1 | HoldingRegister | 40010 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PS Nav. Spr. (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PS_Nav_Spr_MAINOpTime | 1 | HoldingRegister | 40012 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | PS Nav. Spr. (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.PS_Nav_Spr_BACKUPOpTime | 1 | HoldingRegister | 40014 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Anchor_Aft_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Anchor AFT (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Anchor_Aft_MAINOpTime | 1 | HoldingRegister | 40016 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Anchor AFT (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Anchor_Aft_BACKUPOpTime | 1 | HoldingRegister | 40018 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Main_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Main (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Main_MAINOpTime | 1 | HoldingRegister | 40020 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Main_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Main (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Main_BACKUPOpTime | 1 | HoldingRegister | 40022 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Mizz_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Mizz. (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Mizz_MAINOpTime | 1 | HoldingRegister | 40024 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Steam. Mizz. (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Steam_Mizz_BACKUPOpTime | 1 | HoldingRegister | 40026 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_SB180_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC Stb180° (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_SB180_MAINOpTime | 1 | HoldingRegister | 40028 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_SB180_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC Stb180° (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_SB180_BACKUPOpTime | 1 | HoldingRegister | 40030 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_PS180_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC PS 180° (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_PS180_MAINOpTime | 1 | HoldingRegister | 40032 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_PS180_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC PS 180° (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_PS180_BACKUPOpTime | 1 | HoldingRegister | 40034 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_SB180_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing SB 180° (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_SB180_MAINOpTime | 1 | HoldingRegister | 40036 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing SB 180° (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_SB180_BACKUPOpTime | 1 | HoldingRegister | 40038 | [7 empty] | Minutes
R1.10 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_PS180_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing PS 180° (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_PS180_MAINOpTime | 1 | HoldingRegister | 40040 | [7 empty] | Minutes
R1.10 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Sailing PS 180° (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Sailing_PS180_BACKUPOpTime | 1 | HoldingRegister | 40042 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC & Sailing (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_and_Sailing_MAINOpTime | 1 | HoldingRegister | 40044 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | NUC & Sailing (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.NUC_and_Sailing_BACKUPOpTime | 1 | HoldingRegister | 40046 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Stern_MAINOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Stern (MAIN) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Stern_MAINOpTime | 1 | HoldingRegister | 40048 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Stern_BACKUPOpTime | +CB.2 |  | 1000 | 450000 NAVIGATION LIGHTS |  | Stern (BACKUP) Operating Time | [6 empty] | Mqtt1 |  | 450000 NAVIGATION LIGHTS | $.Stern_BACKUPOpTime | 1 | HoldingRegister | 40050 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | HoldingRegister | 40052 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [10 empty] | 1 | HoldingRegister | 40054 | [7 empty] | Minutes
| True | [13 empty] | Serial Interface - AC Breakers +10P0.1 - AC DISTRIBUTION BOARD 400/230V PANEL 1
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Voltage_A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Voltage_B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.RMS_Voltage_C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Total Active Power | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Iridium GMDSS Supply Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/iridium-gmdss-supply | $.Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Voltage_A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Voltage_B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Voltage_C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Total Active Power | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit Offline Filter Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Voltage_A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Voltage_B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Voltage_C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Voltage_A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Voltage_B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.RMS_Voltage_C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Total Active Power | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | EREC 1 Power Supply Heat Recovery Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/erec-1-power-supply-heat-recovery | $.Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Voltage_A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Voltage_B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.RMS_Voltage_C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Owners State Room Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu-owners-state-room | $.Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Voltage_A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Voltage_B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.RMS_Voltage_C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Total Active Power | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Propulsion Unit AC Heating Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-ac-heating | $.Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Voltage_A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Voltage_B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.RMS_Voltage_C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Total Active Power | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Potable Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/potable-water | $.Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Voltage_A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Voltage_B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.RMS_Voltage_C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 1 PS Deck Locker Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-pump-1-ps-deck-locker | $.Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Voltage_A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Voltage_B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.RMS_Voltage_C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Drain Pump 3 PS Deck Locker Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-pump-3-ps-deck-locker | $.Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Voltage_A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Voltage_B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.RMS_Voltage_C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Total Active Power | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Bilge Water Separator Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/bilge-water-separator | $.Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.RMS_Voltage_C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/draink-tank-mast | $.Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Voltage_A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Voltage_B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Voltage_C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Total Active Power | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Watermaker Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Voltage_A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Voltage_B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.RMS_Voltage_C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pumps Aft Technical Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-aft-technical-water | $.Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Voltage_A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Voltage_B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/co2 | $.RMS_Voltage_C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Co2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/co2 | $.Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Voltage_A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Voltage_B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.RMS_Voltage_C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Antifouling System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/antifouling-system | $.Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Voltage_A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Voltage_B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.RMS_Voltage_C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/adsorption-unit | $.Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Voltage_A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Voltage_B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Voltage_C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Voltage_A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Voltage_B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.RMS_Voltage_C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Hydrophore 1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/hydrophore-1 | $.Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Voltage_A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Voltage_B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.RMS_Voltage_C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump Adiabtic Pump Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-adiabtic-pump | $.Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Voltage_A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Voltage_B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.RMS_Voltage_C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Main Salon JB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb | $.Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Voltage_A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Voltage_B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.RMS_Voltage_C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Total Active Power | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Distrbution Panel 115V Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/distrbution-panel-115v | $.Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Voltage_A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Voltage_B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.RMS_Voltage_C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Master Cabin PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-master-cabin-ps | $.Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Voltage_A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Voltage_B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.RMS_Voltage_C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps | $.Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Voltage_A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Voltage_B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.RMS_Voltage_C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Guest PS And Overflow Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-guest-ps-and-overflow | $.Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Voltage_A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Voltage_B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.RMS_Voltage_C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Charger Radio Batteries (GMDSS) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/charger-radio-batteries-gmdss | $.Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Voltage_A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Voltage_B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.RMS_Voltage_C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 1) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-1 | $.Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Voltage_A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Voltage_B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.RMS_Voltage_C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Underwater Lights PS (Group 2) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-ps-group-2 | $.Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Voltage_A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Voltage_B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.RMS_Voltage_C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU EXH2000 Above Laundry Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu-exh2000-above-laundry | $.Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Voltage_A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Voltage_B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Voltage_C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Discharge Pump Galley/Crew Mess Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Current_Phase_A | 33 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Current_Phase_B | 33 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Current_Phase_C | 33 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Current_Phase_Neut | 33 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Voltage_A_N | 33 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Voltage_B_N | 33 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.RMS_Voltage_C_N | 33 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Active_Power_Phase_A | 33 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Active_Power_Phase_B | 33 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Active_Power_Phase_C | 33 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Total Active Power | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Total_Active_Power | 33 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Power_Factor_Phase_A | 33 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Power_Factor_Phase_B | 33 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Power_Factor_Phase_C | 33 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Ship Office Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/display-switching-ship-office | $.Total_Power_Factor | 33 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Current_Phase_A | 34 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Current_Phase_B | 34 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Current_Phase_C | 34 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Current_Phase_Neut | 34 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Voltage_A_N | 34 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Voltage_B_N | 34 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.RMS_Voltage_C_N | 34 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Active_Power_Phase_A | 34 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Active_Power_Phase_B | 34 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Active_Power_Phase_C | 34 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Total_Active_Power | 34 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Power_Factor_Phase_A | 34 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Power_Factor_Phase_B | 34 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Power_Factor_Phase_C | 34 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Display Switching Supply Helm PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/display-switching-supply-helm-ps | $.Total_Power_Factor | 34 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Current_Phase_A | 35 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Current_Phase_B | 35 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Current_Phase_C | 35 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Current_Phase_Neut | 35 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Voltage_A_N | 35 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Voltage_B_N | 35 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.RMS_Voltage_C_N | 35 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Active_Power_Phase_A | 35 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Active_Power_Phase_B | 35 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Active_Power_Phase_C | 35 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Total_Active_Power | 35 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Power_Factor_Phase_A | 35 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Power_Factor_Phase_B | 35 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Power_Factor_Phase_C | 35 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | ECDIS 1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ecdis-1 | $.Total_Power_Factor | 35 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Current_Phase_A | 36 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Current_Phase_B | 36 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Current_Phase_C | 36 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Current_Phase_Neut | 36 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Voltage_A_N | 36 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Voltage_B_N | 36 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.RMS_Voltage_C_N | 36 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Active_Power_Phase_A | 36 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Active_Power_Phase_B | 36 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Active_Power_Phase_C | 36 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Total_Active_Power | 36 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Power_Factor_Phase_A | 36 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Power_Factor_Phase_B | 36 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Power_Factor_Phase_C | 36 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Radar 1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/radar-1 | $.Total_Power_Factor | 36 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Current_Phase_A | 37 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Current_Phase_B | 37 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Current_Phase_C | 37 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Current_Phase_Neut | 37 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Voltage_A_N | 37 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Voltage_B_N | 37 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.RMS_Voltage_C_N | 37 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Active_Power_Phase_A | 37 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Active_Power_Phase_B | 37 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Active_Power_Phase_C | 37 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Total Active Power | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Total_Active_Power | 37 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Power_Factor_Phase_A | 37 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Power_Factor_Phase_B | 37 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Power_Factor_Phase_C | 37 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Speedlog Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/speedlog | $.Total_Power_Factor | 37 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Current_Phase_A | 38 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Current_Phase_B | 38 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Current_Phase_C | 38 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Current_Phase_Neut | 38 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Voltage_A_N | 38 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Voltage_B_N | 38 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.RMS_Voltage_C_N | 38 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Active_Power_Phase_A | 38 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Active_Power_Phase_B | 38 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Active_Power_Phase_C | 38 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Total_Active_Power | 38 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Power_Factor_Phase_A | 38 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Power_Factor_Phase_B | 38 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Power_Factor_Phase_C | 38 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | VHF 1 (Main) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/vhf-1-main | $.Total_Power_Factor | 38 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Current_Phase_A | 39 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Current_Phase_B | 39 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Current_Phase_C | 39 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Current_Phase_Neut | 39 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Voltage_A_N | 39 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Voltage_B_N | 39 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.RMS_Voltage_C_N | 39 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Active_Power_Phase_A | 39 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Active_Power_Phase_B | 39 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Active_Power_Phase_C | 39 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Total_Active_Power | 39 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Power_Factor_Phase_A | 39 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Power_Factor_Phase_B | 39 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Power_Factor_Phase_C | 39 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | AHU Technical Room Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu-technical-room | $.Total_Power_Factor | 39 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Current_Phase_A | 40 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Current_Phase_B | 40 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Current_Phase_C | 40 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Current_Phase_Neut | 40 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Voltage_A_N | 40 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Voltage_B_N | 40 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.RMS_Voltage_C_N | 40 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Active_Power_Phase_A | 40 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Active_Power_Phase_B | 40 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Active_Power_Phase_C | 40 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Total_Active_Power | 40 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Power_Factor_Phase_A | 40 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Power_Factor_Phase_B | 40 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Power_Factor_Phase_C | 40 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Central Panel Smart Ventilation System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/central-panel-smart-ventilation-system | $.Total_Power_Factor | 40 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Current_Phase_A | 41 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Current_Phase_B | 41 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Current_Phase_C | 41 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Current_Phase_Neut | 41 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Voltage_A_N | 41 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Voltage_B_N | 41 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.RMS_Voltage_C_N | 41 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Active_Power_Phase_A | 41 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Active_Power_Phase_B | 41 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Active_Power_Phase_C | 41 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Total_Active_Power | 41 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Power_Factor_Phase_A | 41 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Power_Factor_Phase_B | 41 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Power_Factor_Phase_C | 41 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | BNWAS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/bnwas | $.Total_Power_Factor | 41 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Current_Phase_A | 42 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Current_Phase_B | 42 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Current_Phase_C | 42 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Current_Phase_Neut | 42 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Voltage_A_N | 42 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Voltage_B_N | 42 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/gps | $.RMS_Voltage_C_N | 42 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/gps | $.Active_Power_Phase_A | 42 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/gps | $.Active_Power_Phase_B | 42 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/gps | $.Active_Power_Phase_C | 42 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/gps | $.Total_Active_Power | 42 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/gps | $.Power_Factor_Phase_A | 42 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/gps | $.Power_Factor_Phase_B | 42 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/gps | $.Power_Factor_Phase_C | 42 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | GPS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/gps | $.Total_Power_Factor | 42 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Current_Phase_A | 43 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Current_Phase_B | 43 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Current_Phase_C | 43 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Current_Phase_Neut | 43 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Voltage_A_N | 43 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Voltage_B_N | 43 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.RMS_Voltage_C_N | 43 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.Active_Power_Phase_A | 43 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.Active_Power_Phase_B | 43 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.Active_Power_Phase_C | 43 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Locker Ventilation Total Active Power | [6 empty] | Mqtt1 |  | power-tag/locker-ventilation | $.Total_Active_Power | 43 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Power_Factor_Phase_A | 43 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Power_Factor_Phase_B | 43 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Power_Factor_Phase_C | 43 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Total_Power_Factor | 43 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Current_Phase_A | 44 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Current_Phase_B | 44 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Current_Phase_C | 44 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Current_Phase_Neut | 44 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Voltage_A_N | 44 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Voltage_B_N | 44 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.RMS_Voltage_C_N | 44 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Active_Power_Phase_A | 44 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Active_Power_Phase_B | 44 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Active_Power_Phase_C | 44 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Peplink 5G Total Active Power | [6 empty] | Mqtt1 |  | power-tag/peplink-5g | $.Total_Active_Power | 44 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Power_Factor_Phase_A | 44 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Power_Factor_Phase_B | 44 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Power_Factor_Phase_C | 44 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Total_Power_Factor | 44 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Current_Phase_A | 45 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Current_Phase_B | 45 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Current_Phase_C | 45 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Current_Phase_Neut | 45 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Voltage_A_N | 45 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Voltage_B_N | 45 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.RMS_Voltage_C_N | 45 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Active_Power_Phase_A | 45 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Active_Power_Phase_B | 45 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Active_Power_Phase_C | 45 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Total Active Power | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Total_Active_Power | 45 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Power_Factor_Phase_A | 45 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Power_Factor_Phase_B | 45 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Power_Factor_Phase_C | 45 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Transfer Pump 1 Grey/Black Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-1-grey-black-water | $.Total_Power_Factor | 45 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Current_Phase_A | 46 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Current_Phase_B | 46 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Current_Phase_C | 46 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Current_Phase_Neut | 46 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Voltage_A_N | 46 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Voltage_B_N | 46 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.RMS_Voltage_C_N | 46 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Active_Power_Phase_A | 46 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Active_Power_Phase_B | 46 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Active_Power_Phase_C | 46 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Total_Active_Power | 46 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Power_Factor_Phase_A | 46 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Power_Factor_Phase_B | 46 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Power_Factor_Phase_C | 46 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump System Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-system-water | $.Total_Power_Factor | 46 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Current_Phase_A | 47 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Current_Phase_B | 47 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Current_Phase_C | 47 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Current_Phase_Neut | 47 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Voltage_A_N | 47 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Voltage_B_N | 47 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.RMS_Voltage_C_N | 47 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Active_Power_Phase_A | 47 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Active_Power_Phase_B | 47 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Active_Power_Phase_C | 47 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Total_Active_Power | 47 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Power_Factor_Phase_A | 47 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Power_Factor_Phase_B | 47 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Power_Factor_Phase_C | 47 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Sea Water Cooling Pump 1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sea-water-cooling-pump-1 | $.Total_Power_Factor | 47 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Current_Phase_A | 48 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Current_Phase_B | 48 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Current_Phase_C | 48 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Current_Phase_Neut | 48 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Voltage_A_N | 48 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Voltage_B_N | 48 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.RMS_Voltage_C_N | 48 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Active_Power_Phase_A | 48 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Active_Power_Phase_B | 48 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Active_Power_Phase_C | 48 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Total Active Power | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Total_Active_Power | 48 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Power_Factor_Phase_A | 48 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Power_Factor_Phase_B | 48 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Power_Factor_Phase_C | 48 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Technical Space Ventilator - In Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-in | $.Total_Power_Factor | 48 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Current_Phase_A | 49 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Current_Phase_B | 49 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Current_Phase_C | 49 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Current_Phase_Neut | 49 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Voltage_A_N | 49 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Voltage_B_N | 49 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.RMS_Voltage_C_N | 49 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Active_Power_Phase_A | 49 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Active_Power_Phase_B | 49 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Active_Power_Phase_C | 49 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Total_Active_Power | 49 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Power_Factor_Phase_A | 49 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Power_Factor_Phase_B | 49 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Power_Factor_Phase_C | 49 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Fresh Air Unit Aft Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-aft-ship | $.Total_Power_Factor | 49 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Current_Phase_A | 50 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Current_Phase_B | 50 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Current_Phase_C | 50 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Current_Phase_Neut | 50 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Voltage_A_N | 50 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Voltage_B_N | 50 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.RMS_Voltage_C_N | 50 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Active_Power_Phase_A | 50 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Active_Power_Phase_B | 50 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Active_Power_Phase_C | 50 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Total_Active_Power | 50 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Power_Factor_Phase_A | 50 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Power_Factor_Phase_B | 50 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Power_Factor_Phase_C | 50 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Extraction Unit Aft Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-aft-ship | $.Total_Power_Factor | 50 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Current_Phase_A | 51 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Current_Phase_B | 51 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Current_Phase_C | 51 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Current_Phase_Neut | 51 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Voltage_A_N | 51 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Voltage_B_N | 51 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.RMS_Voltage_C_N | 51 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Active_Power_Phase_A | 51 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Active_Power_Phase_B | 51 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Active_Power_Phase_C | 51 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Total_Active_Power | 51 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Power_Factor_Phase_A | 51 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Power_Factor_Phase_B | 51 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Power_Factor_Phase_C | 51 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Power Distr. Panel Aft -10P1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-aft-10p1 | $.Total_Power_Factor | 51 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Current_Phase_A | 52 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Current_Phase_B | 52 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Current_Phase_C | 52 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Current_Phase_Neut | 52 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Voltage_A_N | 52 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Voltage_B_N | 52 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.RMS_Voltage_C_N | 52 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Active_Power_Phase_A | 52 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Active_Power_Phase_B | 52 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Active_Power_Phase_C | 52 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Total Active Power | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Total_Active_Power | 52 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Power_Factor_Phase_A | 52 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Power_Factor_Phase_B | 52 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Power_Factor_Phase_C | 52 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Dishwasher Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/dishwasher | $.Total_Power_Factor | 52 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Current_Phase_A | 53 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Current_Phase_B | 53 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Current_Phase_C | 53 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Current_Phase_Neut | 53 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Voltage_A_N | 53 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Voltage_B_N | 53 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.RMS_Voltage_C_N | 53 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Active_Power_Phase_A | 53 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Active_Power_Phase_B | 53 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Active_Power_Phase_C | 53 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Total_Active_Power | 53 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Power_Factor_Phase_A | 53 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Power_Factor_Phase_B | 53 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Power_Factor_Phase_C | 53 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Cooling Water Pump Main Propulsion Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-main-propulsion-unit | $.Total_Power_Factor | 53 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Current_Phase_A | 54 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Current_Phase_B | 54 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Current_Phase_C | 54 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Current_Phase_Neut | 54 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Voltage_A_N | 54 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Voltage_B_N | 54 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.RMS_Voltage_C_N | 54 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Active_Power_Phase_A | 54 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Active_Power_Phase_B | 54 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Active_Power_Phase_C | 54 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Total_Active_Power | 54 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Power_Factor_Phase_A | 54 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Power_Factor_Phase_B | 54 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Power_Factor_Phase_C | 54 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Compressor 1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/compressor-1 | $.Total_Power_Factor | 54 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Current_Phase_A | 55 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Current_Phase_B | 55 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Current_Phase_C | 55 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Current_Phase_Neut | 55 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Voltage_A_N | 55 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Voltage_B_N | 55 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.RMS_Voltage_C_N | 55 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Active_Power_Phase_A | 55 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Active_Power_Phase_B | 55 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Active_Power_Phase_C | 55 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Total Active Power | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Total_Active_Power | 55 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Power_Factor_Phase_A | 55 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Power_Factor_Phase_B | 55 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Power_Factor_Phase_C | 55 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Heat Recovery Pump Compression Chiller Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/heat-recovery-pump-compression-chiller | $.Total_Power_Factor | 55 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_A | 56 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_B | 56 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_C | 56 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_Neut | 56 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Voltage_A_N | 56 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Voltage_B_N | 56 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Voltage_C_N | 56 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Active_Power_Phase_A | 56 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Active_Power_Phase_B | 56 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Active_Power_Phase_C | 56 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Total_Active_Power | 56 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Power_Factor_Phase_A | 56 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Power_Factor_Phase_B | 56 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Power_Factor_Phase_C | 56 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Total_Power_Factor | 56 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_A | 57 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_B | 57 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_C | 57 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Current_Phase_Neut | 57 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Voltage_A_N | 57 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Voltage_B_N | 57 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.RMS_Voltage_C_N | 57 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Active_Power_Phase_A | 57 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Active_Power_Phase_B | 57 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Active_Power_Phase_C | 57 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Total_Active_Power | 57 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Power_Factor_Phase_A | 57 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Power_Factor_Phase_B | 57 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Power_Factor_Phase_C | 57 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Circulation Pump PVT Panles Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panles-fwd | $.Total_Power_Factor | 57 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Current_Phase_A | 58 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Current_Phase_B | 58 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Current_Phase_C | 58 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Current_Phase_Neut | 58 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Voltage_A_N | 58 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Voltage_B_N | 58 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.RMS_Voltage_C_N | 58 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Active_Power_Phase_A | 58 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Active_Power_Phase_B | 58 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Active_Power_Phase_C | 58 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Total_Active_Power | 58 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Power_Factor_Phase_A | 58 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Power_Factor_Phase_B | 58 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Power_Factor_Phase_C | 58 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-fwd | $.Total_Power_Factor | 58 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Current_Phase_A | 59 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Current_Phase_B | 59 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Current_Phase_C | 59 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Current_Phase_Neut | 59 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Voltage_A_N | 59 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Voltage_B_N | 59 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.RMS_Voltage_C_N | 59 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Active_Power_Phase_A | 59 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Active_Power_Phase_B | 59 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Active_Power_Phase_C | 59 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Total_Active_Power | 59 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Power_Factor_Phase_A | 59 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Power_Factor_Phase_B | 59 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Power_Factor_Phase_C | 59 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.1 |  | Battery Room Ventilator PS Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-ps-aft | $.Total_Power_Factor | 59 | HoldingRegister | 3084 | [7 empty] | -
R2.10 | True | [13 empty] | Serial Interface - AC Breakers +10P0.3 - AC DISTRIBUTION BOARD 400/230V PANEL 3
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Voltage_A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Voltage_B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.RMS_Voltage_C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sewage Treatment Plant Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sewage-treatment-plant | $.Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Voltage_A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Voltage_B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.RMS_Voltage_C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Total Active Power | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Propulsion Unit Offline Filter Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/main-propulsion-unit-offline-filter | $.Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Voltage_A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Voltage_B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.RMS_Voltage_C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | AHU2000T Crew Mess Room Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-mess-room | $.Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Voltage_A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Voltage_B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.RMS_Voltage_C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fwd-main-propulsion-unit-ac-heating | $.Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Voltage_A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Voltage_B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.RMS_Voltage_C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Submersible Bilge Pump 3 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/submersible-bilge-pump-3 | $.Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.RMS_Voltage_C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-tank-airco | $.Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Voltage_A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Voltage_B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.RMS_Voltage_C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Total Active Power | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Watermaker Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/watermaker | $.Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Voltage_A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Voltage_B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.RMS_Voltage_C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Hydrophore 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/hydrophore-2 | $.Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Voltage_A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Voltage_B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.RMS_Voltage_C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chlorine Dosing Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/chlorine-dosing-unit | $.Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Voltage_A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Voltage_B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.RMS_Voltage_C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Total Active Power | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Quooker Salon Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/quooker-salon | $.Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Voltage_A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Voltage_B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.RMS_Voltage_C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Main Salon Jb 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/main-salon-jb-2 | $.Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Voltage_A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Voltage_B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.RMS_Voltage_C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Total Active Power | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Serv. Corridor Jb Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/serv-corridor-jb | $.Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Voltage_A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Voltage_B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.RMS_Voltage_C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Total Active Power | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Galley Drain Pump Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/galley-drain-pump | $.Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Voltage_A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Voltage_B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.RMS_Voltage_C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Helmstation PS/SB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/kvm-helmstation-ps-sb | $.Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Voltage_A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Voltage_B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.RMS_Voltage_C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 1) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-1 | $.Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Voltage_A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Voltage_B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.RMS_Voltage_C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Underwater Lights SB (Group 2) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/underwater-lights-sb-group-2 | $.Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Voltage_A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Voltage_B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.RMS_Voltage_C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Lighting Technical Space Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lighting-technical-space | $.Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Voltage_A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Voltage_B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.RMS_Voltage_C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fan Coil Engine Office Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fan-coil-engine-office | $.Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Voltage_A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Voltage_B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.RMS_Voltage_C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Sockets Main Technical Space Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sockets-main-technical-space | $.Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Voltage_A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Voltage_B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.RMS_Voltage_C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | ECDIS 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ecdis-2 | $.Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Voltage_A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Voltage_B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.RMS_Voltage_C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Total Active Power | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Captains Cabin Ships Office Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/kvm-captains-cabin-ships-office | $.Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Voltage_A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Voltage_B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.RMS_Voltage_C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Total Active Power | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/kvm-mission-room-nav-comm-locker-fwd-rack | $.Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Voltage_A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Voltage_B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.RMS_Voltage_C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Total Active Power | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | EREC 2 Power Supply Heat Recovery Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/erec-2-power-supply-heat-recovery | $.Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Voltage_A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Voltage_B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Voltage_C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Total Active Power | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Voltage_A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Voltage_B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.RMS_Voltage_C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Total Active Power | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 3 Greywater Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-3-greywater | $.Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Voltage_A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Voltage_B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.RMS_Voltage_C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Total Active Power | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Dirty Oil Pump Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/dirty-oil-pump | $.Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Voltage_A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Voltage_B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.RMS_Voltage_C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Total Active Power | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Transfer Pump 2 Black Water Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/transfer-pump-2-black-water | $.Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Voltage_A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Voltage_B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.RMS_Voltage_C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Total Active Power | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Technical Space Ventilator - Out Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/technical-space-ventilator-out | $.Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Current_Phase_A | 33 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Current_Phase_B | 33 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Current_Phase_C | 33 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Current_Phase_Neut | 33 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Voltage_A_N | 33 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Voltage_B_N | 33 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.RMS_Voltage_C_N | 33 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Active_Power_Phase_A | 33 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Active_Power_Phase_B | 33 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Active_Power_Phase_C | 33 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Total_Active_Power | 33 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Power_Factor_Phase_A | 33 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Power_Factor_Phase_B | 33 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Power_Factor_Phase_C | 33 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Fresh Air Unit Fore Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fresh-air-unit-fore-ship | $.Total_Power_Factor | 33 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Current_Phase_A | 34 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Current_Phase_B | 34 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Current_Phase_C | 34 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Current_Phase_Neut | 34 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Voltage_A_N | 34 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Voltage_B_N | 34 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.RMS_Voltage_C_N | 34 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Active_Power_Phase_A | 34 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Active_Power_Phase_B | 34 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Active_Power_Phase_C | 34 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Total_Active_Power | 34 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Power_Factor_Phase_A | 34 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Power_Factor_Phase_B | 34 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Power_Factor_Phase_C | 34 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Extraction Unit Fore Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/extraction-unit-fore-ship | $.Total_Power_Factor | 34 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Current_Phase_A | 35 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Current_Phase_B | 35 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Current_Phase_C | 35 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Current_Phase_Neut | 35 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Voltage_A_N | 35 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Voltage_B_N | 35 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.RMS_Voltage_C_N | 35 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Active_Power_Phase_A | 35 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Active_Power_Phase_B | 35 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Active_Power_Phase_C | 35 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Total_Active_Power | 35 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Power_Factor_Phase_A | 35 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Power_Factor_Phase_B | 35 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Power_Factor_Phase_C | 35 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Power Distr. Panel Galley - 10P2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/power-distr-panel-galley-10p2 | $.Total_Power_Factor | 35 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Current_Phase_A | 36 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Current_Phase_B | 36 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Current_Phase_C | 36 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Current_Phase_Neut | 36 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Voltage_A_N | 36 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Voltage_B_N | 36 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.RMS_Voltage_C_N | 36 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Active_Power_Phase_A | 36 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Active_Power_Phase_B | 36 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Active_Power_Phase_C | 36 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Total Active Power | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Total_Active_Power | 36 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Power_Factor_Phase_A | 36 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Power_Factor_Phase_B | 36 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Power_Factor_Phase_C | 36 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Pressure Pump Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/pressure-pump | $.Total_Power_Factor | 36 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Current_Phase_A | 37 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Current_Phase_B | 37 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Current_Phase_C | 37 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Current_Phase_Neut | 37 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Voltage_A_N | 37 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Voltage_B_N | 37 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.RMS_Voltage_C_N | 37 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Active_Power_Phase_A | 37 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Active_Power_Phase_B | 37 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Active_Power_Phase_C | 37 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Total_Active_Power | 37 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Power_Factor_Phase_A | 37 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Power_Factor_Phase_B | 37 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Power_Factor_Phase_C | 37 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Chilled Water Pump Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/chilled-water-pump-adsorption-unit | $.Total_Power_Factor | 37 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Current_Phase_A | 38 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Current_Phase_B | 38 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Current_Phase_C | 38 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Current_Phase_Neut | 38 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Voltage_A_N | 38 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Voltage_B_N | 38 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.RMS_Voltage_C_N | 38 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Active_Power_Phase_A | 38 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Active_Power_Phase_B | 38 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Active_Power_Phase_C | 38 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Total_Active_Power | 38 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Power_Factor_Phase_A | 38 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Power_Factor_Phase_B | 38 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Power_Factor_Phase_C | 38 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-fwd-propulstion-unit | $.Total_Power_Factor | 38 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Current_Phase_A | 39 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Current_Phase_B | 39 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Current_Phase_C | 39 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Current_Phase_Neut | 39 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Voltage_A_N | 39 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Voltage_B_N | 39 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.RMS_Voltage_C_N | 39 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Active_Power_Phase_A | 39 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Active_Power_Phase_B | 39 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Active_Power_Phase_C | 39 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Total_Active_Power | 39 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Power_Factor_Phase_A | 39 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Power_Factor_Phase_B | 39 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Power_Factor_Phase_C | 39 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Compressor 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/compressor-2 | $.Total_Power_Factor | 39 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Current_Phase_A | 40 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Current_Phase_B | 40 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Current_Phase_C | 40 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Current_Phase_Neut | 40 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Voltage_A_N | 40 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Voltage_B_N | 40 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.RMS_Voltage_C_N | 40 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Active_Power_Phase_A | 40 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Active_Power_Phase_B | 40 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Active_Power_Phase_C | 40 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Total_Active_Power | 40 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Power_Factor_Phase_A | 40 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Power_Factor_Phase_B | 40 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Power_Factor_Phase_C | 40 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-warm-water-adsorption-unit | $.Total_Power_Factor | 40 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Current_Phase_A | 41 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Current_Phase_B | 41 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Current_Phase_C | 41 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Current_Phase_Neut | 41 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Voltage_A_N | 41 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Voltage_B_N | 41 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.RMS_Voltage_C_N | 41 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Active_Power_Phase_A | 41 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Active_Power_Phase_B | 41 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Active_Power_Phase_C | 41 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Total Active Power | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Total_Active_Power | 41 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Power_Factor_Phase_A | 41 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Power_Factor_Phase_B | 41 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Power_Factor_Phase_C | 41 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Cooling Water Pump Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/cooling-water-pump-adsorption-unit | $.Total_Power_Factor | 41 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Current_Phase_A | 42 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Current_Phase_B | 42 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Current_Phase_C | 42 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Current_Phase_Neut | 42 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Voltage_A_N | 42 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Voltage_B_N | 42 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.RMS_Voltage_C_N | 42 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Active_Power_Phase_A | 42 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Active_Power_Phase_B | 42 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Active_Power_Phase_C | 42 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Total_Active_Power | 42 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Power_Factor_Phase_A | 42 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Power_Factor_Phase_B | 42 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Power_Factor_Phase_C | 42 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circulation Pump PVT Panels Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-pvt-panels-aft | $.Total_Power_Factor | 42 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Current_Phase_A | 43 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Current_Phase_B | 43 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Current_Phase_C | 43 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Current_Phase_Neut | 43 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Voltage_A_N | 43 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Voltage_B_N | 43 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.RMS_Voltage_C_N | 43 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Active_Power_Phase_A | 43 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Active_Power_Phase_B | 43 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Active_Power_Phase_C | 43 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Total_Active_Power | 43 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Power_Factor_Phase_A | 43 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Power_Factor_Phase_B | 43 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Power_Factor_Phase_C | 43 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circ-pump-heat-water-fresh-hotwater-system | $.Total_Power_Factor | 43 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Current_Phase_A | 44 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Current_Phase_B | 44 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Current_Phase_C | 44 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Current_Phase_Neut | 44 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Voltage_A_N | 44 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Voltage_B_N | 44 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.RMS_Voltage_C_N | 44 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Active_Power_Phase_A | 44 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Active_Power_Phase_B | 44 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Active_Power_Phase_C | 44 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Total_Active_Power | 44 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Power_Factor_Phase_A | 44 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Power_Factor_Phase_B | 44 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Power_Factor_Phase_C | 44 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Circ. Pump Cooling Water Electrical System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circ-pump-cooling-water-electrical-system | $.Total_Power_Factor | 44 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Current_Phase_A | 45 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Current_Phase_B | 45 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Current_Phase_C | 45 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Current_Phase_Neut | 45 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Voltage_A_N | 45 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Voltage_B_N | 45 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.RMS_Voltage_C_N | 45 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Active_Power_Phase_A | 45 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Active_Power_Phase_B | 45 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Active_Power_Phase_C | 45 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Total_Active_Power | 45 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Power_Factor_Phase_A | 45 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Power_Factor_Phase_B | 45 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Power_Factor_Phase_C | 45 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-fwd | $.Total_Power_Factor | 45 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Current_Phase_A | 46 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Current_Phase_B | 46 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Current_Phase_C | 46 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Current_Phase_Neut | 46 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Voltage_A_N | 46 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Voltage_B_N | 46 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.RMS_Voltage_C_N | 46 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Active_Power_Phase_A | 46 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Active_Power_Phase_B | 46 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Active_Power_Phase_C | 46 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Total_Active_Power | 46 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Power_Factor_Phase_A | 46 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Power_Factor_Phase_B | 46 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Power_Factor_Phase_C | 46 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Battery Room Ventilator SB Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/battery-room-ventilator-sb-aft | $.Total_Power_Factor | 46 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Current_Phase_A | 47 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Current_Phase_B | 47 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Current_Phase_C | 47 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Current_Phase_Neut | 47 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Voltage_A_N | 47 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Voltage_B_N | 47 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.RMS_Voltage_C_N | 47 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Active_Power_Phase_A | 47 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Active_Power_Phase_B | 47 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Active_Power_Phase_C | 47 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Total Active Power | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Total_Active_Power | 47 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Power_Factor_Phase_A | 47 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Power_Factor_Phase_B | 47 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Power_Factor_Phase_C | 47 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P0.3 |  | Welding Socket Lazarette Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/welding-socket-lazarette | $.Total_Power_Factor | 47 | HoldingRegister | 3084 | [7 empty] | -
R2.10 | True | [13 empty] | Serial Interface - AC Breakers +10P1 - AC DISTRIBUTION BOARD 400/230V AFT GUEST CORRIDOR
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Voltage_A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Voltage_B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.RMS_Voltage_C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Aft Peak Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ventilator-aft-peak | $.Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Voltage_A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Voltage_B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.RMS_Voltage_C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Ventilator Bilge Aft Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-aft-ship | $.Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Voltage_A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Voltage_B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.RMS_Voltage_C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-deck-lounge-guest-cabin-aft-sb | $.Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Voltage_A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Voltage_B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.RMS_Voltage_C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Technical Space Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-technical-space | $.Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Voltage_A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Voltage_B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.RMS_Voltage_C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-cabin-fwd-ps-guest-cabin-aft-ps | $.Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Voltage_A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Voltage_B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.RMS_Voltage_C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-hers-owners-state-room-ps | $.Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Voltage_A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Voltage_B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.RMS_Voltage_C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-bath-his-owners-state-room-sb | $.Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Voltage_A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Voltage_B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.RMS_Voltage_C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Ships Office Watersport Storage Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-ships-office-watersport-storage | $.Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Voltage_A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Voltage_B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.RMS_Voltage_C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-owners-deckh-dining-main-salon-lounge | $.Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Voltage_A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Voltage_B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.RMS_Voltage_C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AHU1500 Aft Area Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu1500-aft-area | $.Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Voltage_A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Voltage_B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.RMS_Voltage_C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Discharge Pump Mast Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-mast | $.Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Voltage_A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Voltage_B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.RMS_Voltage_C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Lights Technical Area Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lights-technical-area | $.Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Voltage_A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Voltage_B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.RMS_Voltage_C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-2 | $.Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Voltage_A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Voltage_B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.RMS_Voltage_C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 3 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-3 | $.Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Voltage_A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Voltage_B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.RMS_Voltage_C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP125 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp125 | $.Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Voltage_A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Voltage_B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.RMS_Voltage_C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner - EMP126 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-emp126 | $.Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Voltage_A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Voltage_B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.RMS_Voltage_C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Guest Cabin 4 - EMP124 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-4-emp124 | $.Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Voltage_A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Voltage_B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.RMS_Voltage_C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Lower Deck Lounge - EMP121 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-lower-deck-lounge-emp121 | $.Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Voltage_A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Voltage_B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.RMS_Voltage_C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Outlets Owner Private Lounge - EMP220 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-owner-private-lounge-emp220 | $.Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Voltage_A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Voltage_B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.RMS_Voltage_C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | KNX Supply - EMP121 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/knx-supply-emp121 | $.Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Voltage_A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Voltage_B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Voltage_C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Total Active Power | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Voltage_A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Voltage_B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/starlink | $.RMS_Voltage_C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Total Active Power | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Starlink Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/starlink | $.Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Voltage_A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Voltage_B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.RMS_Voltage_C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Total Active Power | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Diving Compressor Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/diving-compressor | $.Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Voltage_A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Voltage_B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.RMS_Voltage_C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Burglar Alarm System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/burglar-alarm-system | $.Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Voltage_A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Voltage_B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.RMS_Voltage_C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | AV System Supply #1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-1 | $.Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Voltage_A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Voltage_B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.RMS_Voltage_C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Sliding Window Private Salon Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sliding-window-private-salon | $.Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Voltage_A_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Voltage_A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Voltage_B_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Voltage_B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Voltage_C_N | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.RMS_Voltage_C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Total Active Power | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR 10P1 |  | Supply Greenwall Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/supply-greenwall | $.Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.10 | True | [13 empty] | Serial Interface - AC Breakers +10P2 - AC DISTRIBUTION BOARD 400/230V GALLEY
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Voltage_A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Voltage_B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.RMS_Voltage_C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Total Active Power | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Induction Cooktop Galley Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/induction-cooktop-galley | $.Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Voltage_A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Voltage_B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.RMS_Voltage_C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-1 | $.Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Voltage_A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Voltage_B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.RMS_Voltage_C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Dishwasher Galley-2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/dishwasher-galley-2 | $.Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Voltage_A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Voltage_B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.RMS_Voltage_C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Total Active Power | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Oven Galley Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/oven-galley | $.Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Voltage_A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Voltage_B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.RMS_Voltage_C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Total Active Power | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Steam Oven Galley Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/steam-oven-galley | $.Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Voltage_A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Voltage_B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.RMS_Voltage_C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Total Active Power | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Service Sink Galley Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/quooker-service-sink-galley | $.Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Voltage_A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Voltage_B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.RMS_Voltage_C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Total Active Power | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Quooker Chef Sink Galley Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/quooker-chef-sink-galley | $.Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Voltage_A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Voltage_B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.RMS_Voltage_C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/galley-jb-1 | $.Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Voltage_A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Voltage_B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.RMS_Voltage_C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley JB-2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/galley-jb-2 | $.Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Voltage_A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Voltage_B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.RMS_Voltage_C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Total Active Power | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Walk In Freezer Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/walk-in-freezer | $.Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Voltage_A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Voltage_B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fridge | $.RMS_Voltage_C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Fridge Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fridge | $.Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Voltage_A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Voltage_B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.RMS_Voltage_C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Fridge System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/compressor-fridge-system | $.Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Voltage_A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Voltage_B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.RMS_Voltage_C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Compressor Freeze System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/compressor-freeze-system | $.Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Voltage_A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Voltage_B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.RMS_Voltage_C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Discharge Pump Galley/Crew Mess Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-galley-crew-mess | $.Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Voltage_A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Voltage_B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.RMS_Voltage_C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-2 | $.Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Voltage_A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Voltage_B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.RMS_Voltage_C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Socket Circuit 3 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/socket-circuit-3 | $.Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Voltage_A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Voltage_B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.RMS_Voltage_C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Fridge System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/evaporator-fridge-system | $.Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Voltage_A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Voltage_B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.RMS_Voltage_C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Evaporator Freeze System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/evaporator-freeze-system | $.Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Voltage_A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Voltage_B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.RMS_Voltage_C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Circulation Pump Cooling Set Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-cooling-set | $.Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Voltage_A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Voltage_B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.RMS_Voltage_C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Total Active Power | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Drain Pump Galley Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/drain-pump-galley | $.Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Voltage_A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Voltage_B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.RMS_Voltage_C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-aft | $.Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Voltage_A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Voltage_B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.RMS_Voltage_C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | FCU: Galley Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-galley-fwd | $.Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Voltage_A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Voltage_B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.RMS_Voltage_C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Total Active Power | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Galley Hood Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/galley-hood | $.Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Voltage_A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Voltage_B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Voltage_C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Voltage_A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Voltage_B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.RMS_Voltage_C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P2 |  | Outlets Galley - EMP 111 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-galley-emp-111 | $.Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.10 | True | [13 empty] | Serial Interface - AC Breakers +10P3 - AC DISTRIBUTION BOARD 400/230V FWD GUEST CORRIDOR
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Voltage_A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Voltage_B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.RMS_Voltage_C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-1 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/washer-1 | $.Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Voltage_A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Voltage_B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.RMS_Voltage_C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Washer-2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/washer-2 | $.Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Voltage_A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Voltage_B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.RMS_Voltage_C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Total Active Power | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dishwasher Crew Mess Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/dishwasher-crew-mess | $.Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Voltage_A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Voltage_B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.RMS_Voltage_C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Dryer-1 and Dryer-2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/dryer-1-and-dryer-2 | $.Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Voltage_A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Voltage_B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.RMS_Voltage_C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-ps | $.Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Voltage_A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Voltage_B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.RMS_Voltage_C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sockets Crew Cabins SB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sockets-crew-cabins-sb | $.Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Voltage_A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Voltage_B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.RMS_Voltage_C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | MFHF SSB (Main Supply) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/mfhf-ssb-main-supply | $.Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Voltage_A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Voltage_B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.RMS_Voltage_C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Total Active Power | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Sliding Door Crew Corridor Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/sliding-door-crew-corridor | $.Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Voltage_A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Voltage_B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.RMS_Voltage_C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Crew Mess JB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/crew-mess-jb | $.Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Voltage_A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Voltage_B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.RMS_Voltage_C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-fwd | $.Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Voltage_A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Voltage_B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.RMS_Voltage_C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Interiour Siding Door Galley Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/interiour-siding-door-galley-aft | $.Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Voltage_A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Voltage_B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.RMS_Voltage_C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Total Active Power | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Main Companion Way Door System Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/main-companion-way-door-system | $.Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Voltage_A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Voltage_B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.RMS_Voltage_C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Total Active Power | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Entrance Door Aft Deckhouse Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/entrance-door-aft-deckhouse | $.Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Voltage_A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Voltage_B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.RMS_Voltage_C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Total Active Power | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Door Crew Entrance Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/door-crew-entrance | $.Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Voltage_A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Voltage_B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.RMS_Voltage_C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew SB Aft/Mid Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-sb-aft-mid | $.Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Voltage_A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Voltage_B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.RMS_Voltage_C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-crew-ps-mid-sb-fwd | $.Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Voltage_A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Voltage_B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.RMS_Voltage_C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-aft | $.Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Voltage_A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Voltage_B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.RMS_Voltage_C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/circulation-pump-wall-ceiling-cooling-fwd | $.Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Voltage_A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Voltage_B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.RMS_Voltage_C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-2 | $.Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Voltage_A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Voltage_B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.RMS_Voltage_C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 4 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-4 | $.Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Voltage_A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Voltage_B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.RMS_Voltage_C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Wall & Ceiling Cooling Pump Section 5 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/wall-ceiling-cooling-pump-section-5 | $.Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Voltage_A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Voltage_B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.RMS_Voltage_C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Guest Cabin PS Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-guest-cabin-ps-fwd | $.Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Voltage_A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Voltage_B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.RMS_Voltage_C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Total Active Power | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | To Overflow Cabin Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/to-overflow-cabin | $.Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Voltage_A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Voltage_B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.RMS_Voltage_C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Captains Cabin Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-captains-cabin | $.Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Voltage_A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Voltage_B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.RMS_Voltage_C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Aft Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-aft | $.Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Voltage_A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Voltage_B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.RMS_Voltage_C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Mid Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-mid | $.Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Voltage_A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Voltage_B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.RMS_Voltage_C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Mid Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-mid | $.Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Voltage_A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Voltage_B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.RMS_Voltage_C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin SB Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-sb-fwd | $.Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Voltage_A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Voltage_B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.RMS_Voltage_C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Total Active Power | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Toilet Crew Cabin PS Fwd Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/toilet-crew-cabin-ps-fwd | $.Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Voltage_A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Voltage_B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.RMS_Voltage_C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Aft Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lighting-aft-ship | $.Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Voltage_A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Voltage_B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.RMS_Voltage_C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 5) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-5 | $.Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Voltage_A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Voltage_B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.RMS_Voltage_C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lighting Fore Ship (Section 4) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lighting-fore-ship-section-4 | $.Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Current_Phase_A | 33 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Current_Phase_B | 33 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Current_Phase_C | 33 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Current_Phase_Neut | 33 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Voltage_A_N | 33 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Voltage_B_N | 33 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.RMS_Voltage_C_N | 33 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Active_Power_Phase_A | 33 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Active_Power_Phase_B | 33 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Active_Power_Phase_C | 33 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Total_Active_Power | 33 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Power_Factor_Phase_A | 33 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Power_Factor_Phase_B | 33 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Power_Factor_Phase_C | 33 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare (Lighting) Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare-lighting | $.Total_Power_Factor | 33 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Current_Phase_A | 34 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Current_Phase_B | 34 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Current_Phase_C | 34 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Current_Phase_Neut | 34 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Voltage_A_N | 34 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Voltage_B_N | 34 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.RMS_Voltage_C_N | 34 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Active_Power_Phase_A | 34 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Active_Power_Phase_B | 34 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Active_Power_Phase_C | 34 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Total_Active_Power | 34 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Power_Factor_Phase_A | 34 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Power_Factor_Phase_B | 34 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Power_Factor_Phase_C | 34 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Fore Peak Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ventilator-fore-peak | $.Total_Power_Factor | 34 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Current_Phase_A | 35 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Current_Phase_B | 35 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Current_Phase_C | 35 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Current_Phase_Neut | 35 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Voltage_A_N | 35 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Voltage_B_N | 35 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.RMS_Voltage_C_N | 35 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Active_Power_Phase_A | 35 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Active_Power_Phase_B | 35 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Active_Power_Phase_C | 35 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Total_Active_Power | 35 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Power_Factor_Phase_A | 35 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Power_Factor_Phase_B | 35 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Power_Factor_Phase_C | 35 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Ventilator Bilge Fore Ship Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ventilator-bilge-fore-ship | $.Total_Power_Factor | 35 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Current_Phase_A | 36 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Current_Phase_B | 36 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Current_Phase_C | 36 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Current_Phase_Neut | 36 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Voltage_A_N | 36 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Voltage_B_N | 36 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.RMS_Voltage_C_N | 36 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Active_Power_Phase_A | 36 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Active_Power_Phase_B | 36 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Active_Power_Phase_C | 36 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Total_Active_Power | 36 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Power_Factor_Phase_A | 36 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Power_Factor_Phase_B | 36 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Power_Factor_Phase_C | 36 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Guest Fwd Cabin PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-guest-fwd-cabin-ps | $.Total_Power_Factor | 36 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Current_Phase_A | 37 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Current_Phase_B | 37 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Current_Phase_C | 37 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Current_Phase_Neut | 37 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Voltage_A_N | 37 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Voltage_B_N | 37 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.RMS_Voltage_C_N | 37 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Active_Power_Phase_A | 37 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Active_Power_Phase_B | 37 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Active_Power_Phase_C | 37 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Total_Active_Power | 37 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Power_Factor_Phase_A | 37 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Power_Factor_Phase_B | 37 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Power_Factor_Phase_C | 37 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU Overflow Bathroom Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-overflow-bathroom | $.Total_Power_Factor | 37 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Current_Phase_A | 38 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Current_Phase_B | 38 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Current_Phase_C | 38 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Current_Phase_Neut | 38 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Voltage_A_N | 38 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Voltage_B_N | 38 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.RMS_Voltage_C_N | 38 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Active_Power_Phase_A | 38 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Active_Power_Phase_B | 38 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Active_Power_Phase_C | 38 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Total_Active_Power | 38 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Power_Factor_Phase_A | 38 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Power_Factor_Phase_B | 38 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Power_Factor_Phase_C | 38 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-laundry-captain-cabin-crew-cabin-mid-ps | $.Total_Power_Factor | 38 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Current_Phase_A | 39 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Current_Phase_B | 39 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Current_Phase_C | 39 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Current_Phase_Neut | 39 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Voltage_A_N | 39 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Voltage_B_N | 39 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.RMS_Voltage_C_N | 39 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Active_Power_Phase_A | 39 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Active_Power_Phase_B | 39 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Active_Power_Phase_C | 39 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Total_Active_Power | 39 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Power_Factor_Phase_A | 39 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Power_Factor_Phase_B | 39 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Power_Factor_Phase_C | 39 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-mess-crew-cabin-aft-sb-crew-cabin-mid-sb | $.Total_Power_Factor | 39 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Current_Phase_A | 40 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Current_Phase_B | 40 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Current_Phase_C | 40 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Current_Phase_Neut | 40 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Voltage_A_N | 40 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Voltage_B_N | 40 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.RMS_Voltage_C_N | 40 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Active_Power_Phase_A | 40 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Active_Power_Phase_B | 40 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Active_Power_Phase_C | 40 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Total_Active_Power | 40 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Power_Factor_Phase_A | 40 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Power_Factor_Phase_B | 40 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Power_Factor_Phase_C | 40 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-crew-cabin-fwd-ps-crew-cabin-fwd-sb | $.Total_Power_Factor | 40 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Current_Phase_A | 41 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Current_Phase_B | 41 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Current_Phase_C | 41 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Current_Phase_Neut | 41 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Voltage_A_N | 41 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Voltage_B_N | 41 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.RMS_Voltage_C_N | 41 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Active_Power_Phase_A | 41 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Active_Power_Phase_B | 41 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Active_Power_Phase_C | 41 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Total Active Power | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Total_Active_Power | 41 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Power_Factor_Phase_A | 41 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Power_Factor_Phase_B | 41 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Power_Factor_Phase_C | 41 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | FCU: Main Salon Bar Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/fcu-main-salon-bar | $.Total_Power_Factor | 41 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Current_Phase_A | 42 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Current_Phase_B | 42 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Current_Phase_C | 42 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Current_Phase_Neut | 42 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Voltage_A_N | 42 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Voltage_B_N | 42 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.RMS_Voltage_C_N | 42 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Active_Power_Phase_A | 42 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Active_Power_Phase_B | 42 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Active_Power_Phase_C | 42 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Total_Active_Power | 42 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Power_Factor_Phase_A | 42 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Power_Factor_Phase_B | 42 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Power_Factor_Phase_C | 42 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pumps-8/9/10 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pumps-8-9-10 | $.Total_Power_Factor | 42 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Current_Phase_A | 43 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Current_Phase_B | 43 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Current_Phase_C | 43 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Current_Phase_Neut | 43 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Voltage_A_N | 43 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Voltage_B_N | 43 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.RMS_Voltage_C_N | 43 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Active_Power_Phase_A | 43 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Active_Power_Phase_B | 43 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Active_Power_Phase_C | 43 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Total_Active_Power | 43 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Power_Factor_Phase_A | 43 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Power_Factor_Phase_B | 43 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Power_Factor_Phase_C | 43 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - 901JB003 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-901jb003 | $.Total_Power_Factor | 43 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Current_Phase_A | 44 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Current_Phase_B | 44 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Current_Phase_C | 44 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Current_Phase_Neut | 44 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Voltage_A_N | 44 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Voltage_B_N | 44 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.RMS_Voltage_C_N | 44 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Active_Power_Phase_A | 44 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Active_Power_Phase_B | 44 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Active_Power_Phase_C | 44 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Total_Active_Power | 44 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Power_Factor_Phase_A | 44 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Power_Factor_Phase_B | 44 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Power_Factor_Phase_C | 44 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Lights Technical Areas - EMP109 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/lights-technical-areas-emp109 | $.Total_Power_Factor | 44 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Current_Phase_A | 45 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Current_Phase_B | 45 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Current_Phase_C | 45 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Current_Phase_Neut | 45 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Voltage_A_N | 45 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Voltage_B_N | 45 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.RMS_Voltage_C_N | 45 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Active_Power_Phase_A | 45 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Active_Power_Phase_B | 45 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Active_Power_Phase_C | 45 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Total_Active_Power | 45 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Power_Factor_Phase_A | 45 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Power_Factor_Phase_B | 45 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Power_Factor_Phase_C | 45 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 1 - EMP101 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-1-emp101 | $.Total_Power_Factor | 45 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Current_Phase_A | 46 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Current_Phase_B | 46 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Current_Phase_C | 46 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Current_Phase_Neut | 46 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Voltage_A_N | 46 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Voltage_B_N | 46 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.RMS_Voltage_C_N | 46 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Active_Power_Phase_A | 46 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Active_Power_Phase_B | 46 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Active_Power_Phase_C | 46 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Total_Active_Power | 46 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Power_Factor_Phase_A | 46 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Power_Factor_Phase_B | 46 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Power_Factor_Phase_C | 46 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 2 - EMP102 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-2-emp102 | $.Total_Power_Factor | 46 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Current_Phase_A | 47 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Current_Phase_B | 47 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Current_Phase_C | 47 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Current_Phase_Neut | 47 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Voltage_A_N | 47 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Voltage_B_N | 47 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.RMS_Voltage_C_N | 47 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Active_Power_Phase_A | 47 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Active_Power_Phase_B | 47 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Active_Power_Phase_C | 47 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Total_Active_Power | 47 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Power_Factor_Phase_A | 47 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Power_Factor_Phase_B | 47 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Power_Factor_Phase_C | 47 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 3 - EMP103 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-3-emp103 | $.Total_Power_Factor | 47 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Current_Phase_A | 48 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Current_Phase_B | 48 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Current_Phase_C | 48 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Current_Phase_Neut | 48 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Voltage_A_N | 48 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Voltage_B_N | 48 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.RMS_Voltage_C_N | 48 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Active_Power_Phase_A | 48 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Active_Power_Phase_B | 48 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Active_Power_Phase_C | 48 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Total_Active_Power | 48 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Power_Factor_Phase_A | 48 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Power_Factor_Phase_B | 48 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Power_Factor_Phase_C | 48 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 4 - EMP104 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-4-emp104 | $.Total_Power_Factor | 48 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Current_Phase_A | 49 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Current_Phase_B | 49 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Current_Phase_C | 49 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Current_Phase_Neut | 49 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Voltage_A_N | 49 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Voltage_B_N | 49 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.RMS_Voltage_C_N | 49 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Active_Power_Phase_A | 49 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Active_Power_Phase_B | 49 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Active_Power_Phase_C | 49 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Total_Active_Power | 49 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Power_Factor_Phase_A | 49 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Power_Factor_Phase_B | 49 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Power_Factor_Phase_C | 49 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Captains Cabin - EMP105 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-captains-cabin-emp105 | $.Total_Power_Factor | 49 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Current_Phase_A | 50 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Current_Phase_B | 50 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Current_Phase_C | 50 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Current_Phase_Neut | 50 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Voltage_A_N | 50 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Voltage_B_N | 50 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.RMS_Voltage_C_N | 50 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Active_Power_Phase_A | 50 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Active_Power_Phase_B | 50 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Active_Power_Phase_C | 50 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Total_Active_Power | 50 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Power_Factor_Phase_A | 50 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Power_Factor_Phase_B | 50 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Power_Factor_Phase_C | 50 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Cabin 5 - EMP106 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-cabin-5-emp106 | $.Total_Power_Factor | 50 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Current_Phase_A | 51 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Current_Phase_B | 51 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Current_Phase_C | 51 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Current_Phase_Neut | 51 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Voltage_A_N | 51 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Voltage_B_N | 51 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.RMS_Voltage_C_N | 51 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Active_Power_Phase_A | 51 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Active_Power_Phase_B | 51 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Active_Power_Phase_C | 51 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Total_Active_Power | 51 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Power_Factor_Phase_A | 51 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Power_Factor_Phase_B | 51 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Power_Factor_Phase_C | 51 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Laundry - EMP108 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-laundry-emp108 | $.Total_Power_Factor | 51 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Current_Phase_A | 52 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Current_Phase_B | 52 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Current_Phase_C | 52 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Current_Phase_Neut | 52 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Voltage_A_N | 52 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Voltage_B_N | 52 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.RMS_Voltage_C_N | 52 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Active_Power_Phase_A | 52 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Active_Power_Phase_B | 52 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Active_Power_Phase_C | 52 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Total_Active_Power | 52 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Power_Factor_Phase_A | 52 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Power_Factor_Phase_B | 52 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Power_Factor_Phase_C | 52 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Lounge - EMP108 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-lounge-emp108 | $.Total_Power_Factor | 52 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Current_Phase_A | 53 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Current_Phase_B | 53 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Current_Phase_C | 53 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Current_Phase_Neut | 53 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Voltage_A_N | 53 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Voltage_B_N | 53 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.RMS_Voltage_C_N | 53 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Active_Power_Phase_A | 53 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Active_Power_Phase_B | 53 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Active_Power_Phase_C | 53 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Total_Active_Power | 53 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Power_Factor_Phase_A | 53 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Power_Factor_Phase_B | 53 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Power_Factor_Phase_C | 53 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Crew Mess - EMP109 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-crew-mess-emp109 | $.Total_Power_Factor | 53 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Current_Phase_A | 54 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Current_Phase_B | 54 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Current_Phase_C | 54 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Current_Phase_Neut | 54 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Voltage_A_N | 54 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Voltage_B_N | 54 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.RMS_Voltage_C_N | 54 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Active_Power_Phase_A | 54 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Active_Power_Phase_B | 54 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Active_Power_Phase_C | 54 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Total_Active_Power | 54 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Power_Factor_Phase_A | 54 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Power_Factor_Phase_B | 54 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Power_Factor_Phase_C | 54 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Guest Cabin 1 - EMP112 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-guest-cabin-1-emp112 | $.Total_Power_Factor | 54 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Current_Phase_A | 55 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Current_Phase_B | 55 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Current_Phase_C | 55 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Current_Phase_Neut | 55 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Voltage_A_N | 55 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Voltage_B_N | 55 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.RMS_Voltage_C_N | 55 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Active_Power_Phase_A | 55 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Active_Power_Phase_B | 55 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Active_Power_Phase_C | 55 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Total_Active_Power | 55 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Power_Factor_Phase_A | 55 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Power_Factor_Phase_B | 55 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Power_Factor_Phase_C | 55 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Dining - EMP202 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-dining-emp202 | $.Total_Power_Factor | 55 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Current_Phase_A | 56 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Current_Phase_B | 56 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Current_Phase_C | 56 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Current_Phase_Neut | 56 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Voltage_A_N | 56 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Voltage_B_N | 56 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.RMS_Voltage_C_N | 56 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Active_Power_Phase_A | 56 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Active_Power_Phase_B | 56 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Active_Power_Phase_C | 56 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Total_Active_Power | 56 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Power_Factor_Phase_A | 56 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Power_Factor_Phase_B | 56 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Power_Factor_Phase_C | 56 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Outlets Salon - EMP201 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/outlets-salon-emp201 | $.Total_Power_Factor | 56 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Current_Phase_A | 57 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Current_Phase_B | 57 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Current_Phase_C | 57 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Current_Phase_Neut | 57 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Voltage_A_N | 57 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Voltage_B_N | 57 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.RMS_Voltage_C_N | 57 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Active_Power_Phase_A | 57 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Active_Power_Phase_B | 57 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Active_Power_Phase_C | 57 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Total_Active_Power | 57 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Power_Factor_Phase_A | 57 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Power_Factor_Phase_B | 57 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Power_Factor_Phase_C | 57 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP110 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/emp110 | $.Total_Power_Factor | 57 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Current_Phase_A | 58 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Current_Phase_B | 58 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Current_Phase_C | 58 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Current_Phase_Neut | 58 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Voltage_A_N | 58 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Voltage_B_N | 58 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.RMS_Voltage_C_N | 58 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Active_Power_Phase_A | 58 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Active_Power_Phase_B | 58 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Active_Power_Phase_C | 58 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Total_Active_Power | 58 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Power_Factor_Phase_A | 58 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Power_Factor_Phase_B | 58 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Power_Factor_Phase_C | 58 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | EMP113 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/emp113 | $.Total_Power_Factor | 58 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_A | 59 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_B | 59 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_C | 59 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Current_Phase_Neut | 59 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_A_N | 59 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_B_N | 59 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/spare | $.RMS_Voltage_C_N | 59 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_A | 59 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_B | 59 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Active_Power_Phase_C | 59 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Total Active Power | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Active_Power | 59 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_A | 59 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_B | 59 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/spare | $.Power_Factor_Phase_C | 59 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Spare Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/spare | $.Total_Power_Factor | 59 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Current_Phase_A | 60 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Current_Phase_B | 60 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Current_Phase_C | 60 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Current_Phase_Neut | 60 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Voltage_A_N | 60 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Voltage_B_N | 60 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.RMS_Voltage_C_N | 60 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Active_Power_Phase_A | 60 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Active_Power_Phase_B | 60 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Active_Power_Phase_C | 60 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Total Active Power | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Total_Active_Power | 60 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Power_Factor_Phase_A | 60 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Power_Factor_Phase_B | 60 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Power_Factor_Phase_C | 60 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | KNX Supply Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/knx-supply | $.Total_Power_Factor | 60 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Current_Phase_A | 61 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Current_Phase_B | 61 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Current_Phase_C | 61 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Current_Phase_Neut | 61 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Voltage_A_N | 61 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Voltage_B_N | 61 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.RMS_Voltage_C_N | 61 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Active_Power_Phase_A | 61 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Active_Power_Phase_B | 61 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Active_Power_Phase_C | 61 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Total Active Power | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Total_Active_Power | 61 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Power_Factor_Phase_A | 61 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Power_Factor_Phase_B | 61 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Power_Factor_Phase_C | 61 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AV System Supply #2 Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/av-system-supply-2 | $.Total_Power_Factor | 61 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Current_Phase_A | 62 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Current_Phase_B | 62 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Current_Phase_C | 62 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Current_Phase_Neut | 62 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Voltage_A_N | 62 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Voltage_B_N | 62 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.RMS_Voltage_C_N | 62 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Active_Power_Phase_A | 62 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Active_Power_Phase_B | 62 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Active_Power_Phase_C | 62 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Total Active Power | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Total_Active_Power | 62 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Power_Factor_Phase_A | 62 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Power_Factor_Phase_B | 62 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Power_Factor_Phase_C | 62 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | Discharge Pump Captain/Laundry Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/discharge-pump-captain-laundry | $.Total_Power_Factor | 62 | HoldingRegister | 3084 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Current Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Current_Phase_A | 63 | HoldingRegister | 3000 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Current Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Current_Phase_B | 63 | HoldingRegister | 3002 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Current Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Current_Phase_C | 63 | HoldingRegister | 3004 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Current Phase Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Current_Phase_Neut | 63 | HoldingRegister | 3006 | [7 empty] | A
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Voltage_A_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Voltage_A_N | 63 | HoldingRegister | 3028 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Voltage_B_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Voltage_B_N | 63 | HoldingRegister | 3030 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Voltage_C_N | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.RMS_Voltage_C_N | 63 | HoldingRegister | 3032 | [7 empty] | V
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Active Power Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Active_Power_Phase_A | 63 | HoldingRegister | 3054 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Active Power Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Active_Power_Phase_B | 63 | HoldingRegister | 3056 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Active Power Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Active_Power_Phase_C | 63 | HoldingRegister | 3058 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Total Active Power | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Total_Active_Power | 63 | HoldingRegister | 3060 | [7 empty] | W
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Power Factor Phase A | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Power_Factor_Phase_A | 63 | HoldingRegister | 3078 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Power Factor Phase B | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Power_Factor_Phase_B | 63 | HoldingRegister | 3080 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Power Factor Phase C | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Power_Factor_Phase_C | 63 | HoldingRegister | 3082 | [7 empty] | -
R2.10 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR 10P3 |  | AHU2000T Crew Messroom Total Power Factor | [6 empty] | Mqtt1 |  | power-tag/ahu2000t-crew-messroom | $.Total_Power_Factor | 63 | HoldingRegister | 3084 | [7 empty] | -
| True | [13 empty] | Serial Interface - Underwater lighting
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPresetSelection | 4 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftSliderRed | 4 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftSliderGreen | 4 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftSliderBlue | 4 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftSliderWhite | 4 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPresetReset | 4 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPresetSet | 4 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftSliderOnOff | 4 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftActiveChanges | 4 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPreset1HmiColor | 4 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPreset2HmiColor | 4 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPreset3HmiColor | 4 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPreset4HmiColor | 4 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPreset5HmiColor | 4 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftPreset6HmiColor | 4 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR69aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR69aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR69aftCurrentHmiColor | 4 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPresetSelection | 8 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftSliderRed | 8 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftSliderGreen | 8 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftSliderBlue | 8 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftSliderWhite | 8 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPresetReset | 8 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPresetSet | 8 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftSliderOnOff | 8 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftActiveChanges | 8 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPreset1HmiColor | 8 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPreset2HmiColor | 8 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPreset3HmiColor | 8 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPreset4HmiColor | 8 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPreset5HmiColor | 8 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftPreset6HmiColor | 8 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR66aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR66aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR66aftCurrentHmiColor | 8 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPresetSelection | 12 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftSliderRed | 12 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftSliderGreen | 12 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftSliderBlue | 12 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftSliderWhite | 12 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPresetReset | 12 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPresetSet | 12 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftSliderOnOff | 12 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftActiveChanges | 12 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPreset1HmiColor | 12 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPreset2HmiColor | 12 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPreset3HmiColor | 12 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPreset4HmiColor | 12 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPreset5HmiColor | 12 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftPreset6HmiColor | 12 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR57aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR57aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR57aftCurrentHmiColor | 12 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPresetSelection | 16 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftSliderRed | 16 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftSliderGreen | 16 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftSliderBlue | 16 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftSliderWhite | 16 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPresetReset | 16 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPresetSet | 16 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftSliderOnOff | 16 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftActiveChanges | 16 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPreset1HmiColor | 16 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPreset2HmiColor | 16 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPreset3HmiColor | 16 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPreset4HmiColor | 16 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPreset5HmiColor | 16 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftPreset6HmiColor | 16 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR48MidaftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR48MidaftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR48MidaftCurrentHmiColor | 16 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPresetSelection | 20 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdSliderRed | 20 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdSliderGreen | 20 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdSliderBlue | 20 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdSliderWhite | 20 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPresetReset | 20 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPresetSet | 20 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdSliderOnOff | 20 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdActiveChanges | 20 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPreset1HmiColor | 20 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPreset2HmiColor | 20 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPreset3HmiColor | 20 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPreset4HmiColor | 20 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPreset5HmiColor | 20 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdPreset6HmiColor | 20 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR37MidFwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR37MidFwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR37MidFwdCurrentHmiColor | 20 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPresetSelection | 24 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdSliderRed | 24 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdSliderGreen | 24 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdSliderBlue | 24 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdSliderWhite | 24 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPresetReset | 24 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPresetSet | 24 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdSliderOnOff | 24 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdActiveChanges | 24 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPreset1HmiColor | 24 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPreset2HmiColor | 24 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPreset3HmiColor | 24 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPreset4HmiColor | 24 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPreset5HmiColor | 24 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdPreset6HmiColor | 24 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR26FwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR26FwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR26FwdCurrentHmiColor | 24 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPresetSelection | 28 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdSliderRed | 28 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdSliderGreen | 28 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdSliderBlue | 28 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdSliderWhite | 28 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPresetReset | 28 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPresetSet | 28 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdSliderOnOff | 28 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdActiveChanges | 28 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPreset1HmiColor | 28 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPreset2HmiColor | 28 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPreset3HmiColor | 28 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPreset4HmiColor | 28 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPreset5HmiColor | 28 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdPreset6HmiColor | 28 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | PsFR15FwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | PsFR15FwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.PsFR15FwdCurrentHmiColor | 28 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPresetSelection | 32 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdSliderRed | 32 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdSliderGreen | 32 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdSliderBlue | 32 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdSliderWhite | 32 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPresetReset | 32 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPresetSet | 32 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdSliderOnOff | 32 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdActiveChanges | 32 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPreset1HmiColor | 32 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPreset2HmiColor | 32 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPreset3HmiColor | 32 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPreset4HmiColor | 32 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPreset5HmiColor | 32 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdPreset6HmiColor | 32 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR15FwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR15FwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR15FwdCurrentHmiColor | 32 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPresetSelection | 36 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdSliderRed | 36 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdSliderGreen | 36 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdSliderBlue | 36 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdSliderWhite | 36 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPresetReset | 36 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPresetSet | 36 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdSliderOnOff | 36 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdActiveChanges | 36 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPreset1HmiColor | 36 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPreset2HmiColor | 36 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPreset3HmiColor | 36 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPreset4HmiColor | 36 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPreset5HmiColor | 36 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdPreset6HmiColor | 36 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR26FwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR26FwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR26FwdCurrentHmiColor | 36 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPresetSelection | 40 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdSliderRed | 40 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdSliderGreen | 40 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdSliderBlue | 40 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdSliderWhite | 40 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPresetReset | 40 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPresetSet | 40 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdSliderOnOff | 40 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdActiveChanges | 40 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPreset1HmiColor | 40 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPreset2HmiColor | 40 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPreset3HmiColor | 40 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPreset4HmiColor | 40 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPreset5HmiColor | 40 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdPreset6HmiColor | 40 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR37MidFwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR37MidFwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR37MidFwdCurrentHmiColor | 40 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPresetSelection | 44 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftSliderRed | 44 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftSliderGreen | 44 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftSliderBlue | 44 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftSliderWhite | 44 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPresetReset | 44 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPresetSet | 44 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftSliderOnOff | 44 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftActiveChanges | 44 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPreset1HmiColor | 44 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPreset2HmiColor | 44 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPreset3HmiColor | 44 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPreset4HmiColor | 44 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPreset5HmiColor | 44 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftPreset6HmiColor | 44 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR48MidaftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR48MidaftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR48MidaftCurrentHmiColor | 44 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPresetSelection | 48 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftSliderRed | 48 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftSliderGreen | 48 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftSliderBlue | 48 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftSliderWhite | 48 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPresetReset | 48 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPresetSet | 48 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftSliderOnOff | 48 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftActiveChanges | 48 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPreset1HmiColor | 48 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPreset2HmiColor | 48 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPreset3HmiColor | 48 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPreset4HmiColor | 48 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPreset5HmiColor | 48 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftPreset6HmiColor | 48 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR57aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR57aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR57aftCurrentHmiColor | 48 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPresetSelection | 52 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftSliderRed | 52 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftSliderGreen | 52 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftSliderBlue | 52 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftSliderWhite | 52 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPresetReset | 52 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPresetSet | 52 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftSliderOnOff | 52 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftActiveChanges | 52 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPreset1HmiColor | 52 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPreset2HmiColor | 52 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPreset3HmiColor | 52 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPreset4HmiColor | 52 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPreset5HmiColor | 52 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftPreset6HmiColor | 52 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR66aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR66aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR66aftCurrentHmiColor | 52 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPresetSelection | 56 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftSliderRed | 56 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftSliderGreen | 56 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftSliderBlue | 56 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftSliderWhite | 56 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPresetReset | 56 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPresetSet | 56 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftSliderOnOff | 56 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftActiveChanges | 56 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPreset1HmiColor | 56 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPreset2HmiColor | 56 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPreset3HmiColor | 56 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPreset4HmiColor | 56 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPreset5HmiColor | 56 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftPreset6HmiColor | 56 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | SbFR69aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | SbFR69aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.SbFR69aftCurrentHmiColor | 56 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPresetSelection | 60 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdSliderRed | 60 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdSliderGreen | 60 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdSliderBlue | 60 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdSliderWhite | 60 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPresetReset | 60 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPresetSet | 60 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdSliderOnOff | 60 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdActiveChanges | 60 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPreset1HmiColor | 60 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPreset2HmiColor | 60 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPreset3HmiColor | 60 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPreset4HmiColor | 60 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPreset5HmiColor | 60 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdPreset6HmiColor | 60 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM3fwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM3fwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM3fwdCurrentHmiColor | 60 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdSliderRed | 64 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdSliderGreen | 64 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdSliderBlue | 64 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdSliderWhite | 64 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPresetReset | 64 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPresetSet | 64 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdSliderOnOff | 64 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdActiveChanges | 64 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPreset1HmiColor | 64 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPreset2HmiColor | 64 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPreset3HmiColor | 64 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPreset4HmiColor | 64 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPreset5HmiColor | 64 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdPreset6HmiColor | 64 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM4fwdCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM4fwdCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM4fwdCurrentHmiColor | 64 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPresetSelection | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPresetSelection | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPresetSelection | 68 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftSliderRed | 68 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftSliderGreen | 68 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftSliderBlue | 68 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftSliderWhite | 68 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPresetReset | 68 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPresetSet | 68 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftSliderOnOff | 68 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftActiveChanges | 68 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPreset1HmiColor | 68 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPreset2HmiColor | 68 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPreset3HmiColor | 68 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPreset4HmiColor | 68 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPreset5HmiColor | 68 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftPreset6HmiColor | 68 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM1aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM1aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM1aftCurrentHmiColor | 68 |  |  |  | 9
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftSliderRed | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftSliderRed | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftSliderRed | 72 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftSliderGreen | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftSliderGreen | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftSliderGreen | 72 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftSliderBlue | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftSliderBlue | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftSliderBlue | 72 | [9 empty] | #
R2.7 |  | Int16 | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftSliderWhite | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftSliderWhite | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftSliderWhite | 72 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPresetReset | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPresetReset | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPresetReset | 72 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPresetSet | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPresetSet | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPresetSet | 72 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftSliderOnOff | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftSliderOnOff | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftSliderOnOff | 72 | [9 empty] | #
R2.7 |  | Bool | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftActiveChanges | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftActiveChanges | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftActiveChanges | 72 | [9 empty] | #
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPreset1HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPreset1HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPreset1HmiColor | 72 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPreset2HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPreset2HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPreset2HmiColor | 72 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPreset3HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPreset3HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPreset3HmiColor | 72 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPreset4HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPreset4HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPreset4HmiColor | 72 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPreset5HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPreset5HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPreset5HmiColor | 72 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftPreset6HmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftPreset6HmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftPreset6HmiColor | 72 |  |  |  | 9
R2.7 |  | String | KEB1 |  | WriteFieldbus |  |  | True | CAM2aftCurrentHmiColor | +CB.1 |  | 1000 | 450000 UNDERWLIGHTS |  | CAM2aftCurrentHmiColor | [6 empty] | Mqtt1 |  | 450000 UNDERWLIGHTS | $.CAM2aftCurrentHmiColor | 72 |  |  |  | 9
| True | [13 empty] | Serial Interface - KEC3 Port2
| True | [13 empty] | Serial Interface - KEC3 Port3
| True | [13 empty] | Serial Interface - KEC3 Port4
R2.10 |  | Float | PVT |  |  |  |  | True | PVT1_Total_Active_Power | +CB.2 |  | 1000 | PVT |  | PVT1 Total Active Power | [6 empty] | Mqtt1 |  | pvt/pvt1 | $.Total_Active_Power | [10 empty] | -
R2.10 |  | Float | PVT |  |  |  |  | True | PVT1_Total_Power_Factor | +CB.2 |  | 1000 | PVT |  | PVT1 Total Power Factor | [6 empty] | Mqtt1 |  | pvt/pvt1 | $.Total_Power_Factor | [10 empty] | -
R2.10 |  | Float | PVT |  |  |  |  | True | PVT2_Total_Active_Power | +CB.2 |  | 1000 | PVT |  | PVT2 Total Active Power | [6 empty] | Mqtt1 |  | pvt/pvt2 | $.Total_Active_Power | [10 empty] | -
R2.10 |  | Float | PVT |  |  |  |  | True | PVT2_Total_Power_Factor | +CB.2 |  | 1000 | PVT |  | PVT2 Total Power Factor | [6 empty] | Mqtt1 |  | pvt/pvt2 | $.Total_Power_Factor | [10 empty] | -
R2.10 |  | Float | PVT |  |  |  |  | True | PVT3_Total_Active_Power | +CB.2 |  | 1000 | PVT |  | PVT3 Total Active Power | [6 empty] | Mqtt1 |  | pvt/pvt3 | $.Total_Active_Power | [10 empty] | -
R2.10 |  | Float | PVT |  |  |  |  | True | PVT3_Total_Power_Factor | +CB.2 |  | 1000 | PVT |  | PVT3 Total Power Factor | [6 empty] | Mqtt1 |  | pvt/pvt3 | $.Total_Power_Factor | [10 empty] | -
R2.10 |  | Float | Shore |  |  |  |  | True | SHORE1_Total_Active_Power | +CB.2 |  | 1000 | Shore |  | Shore power Total Active Power | [6 empty] | Mqtt1 |  | shore/shore-power | $.Total_Active_Power | [10 empty] | -
R2.10 |  | Float | Shore |  |  |  |  | True | SHORE1_Total_Power_Factor | +CB.2 |  | 1000 | Shore |  | Shore power Total Power Factor | [6 empty] | Mqtt1 |  | shore/shore-power | $.Total_Power_Factor | [10 empty] | -
R2.10 |  | Float | Hydro |  |  |  |  | True | HYDRO1_Total_Active_Power | +CB.2 |  | 1000 | Hydro |  | Thruster1 Total Active Power | [6 empty] | Mqtt1 |  | hydro/thruster1 | $.Total_Active_Power | [10 empty] | -
R2.10 |  | Float | Hydro |  |  |  |  | True | HYDRO1_Total_Power_Factor | +CB.2 |  | 1000 | Hydro |  | Thruster1 Total Power Factor | [6 empty] | Mqtt1 |  | hydro/thruster1 | $.Total_Power_Factor | [10 empty] | -
R2.10 |  | Float | Hydro |  |  |  |  | True | HYDRO2_Total_Active_Power | +CB.2 |  | 1000 | Hydro |  | Thruster2 Total Active Power | [6 empty] | Mqtt1 |  | hydro/thruster2 | $.Total_Active_Power | [10 empty] | -
R2.10 |  | Float | Hydro |  |  |  |  | True | HYDRO2_Total_Power_Factor | +CB.2 |  | 1000 | Hydro |  | Thruster2 Total Power Factor | [6 empty] | Mqtt1 |  | hydro/thruster2 | $.Total_Power_Factor | [10 empty] | -
| True | [13 empty] | EOF

## Help
IO list format
The Chameleon automation system can automatically read an I/O list, but it requires a fixed format. If the customer insists on different column names, we can use alias names which have to be defined custom in the software. The default format of the list:
Mandatory [1] | Name (key) |  | Description | Omschrijving
Yes | Acknowledge location |  | Location where alarm can be acknowledged. This can only be one single location, the location name can be chosen as you wish, but keep in mind to use abbreviations and use it consistently in the IO list. This will be solved by using a pull down list to choose from. | Locatie waar het alarm geaccepteerd kan worden. Dit mag slechts 1 enkele locatie zijn, de naam van de locatie is vrij te kiezen, meestal gebruiken we afkortingen. Let er wel op dat de locatie consequent juist in de lijst wordt ingevuld. Dit zal worden afgedwongen met een pull down lijst.
|  |  | For example: | Enkele voorbeelden;
|  |  | - Wheelhouse: “WH” | - Wheelhouse: “WH”
|  |  | - Engine control room: “ECR” | - Engine control room: “ECR”
|  |  | - Engine room PS: “ERPS” | - Engine room PS: “ERPS”
|  |  | - Tech space below WH: “TSBWH” | - Tech space below WH: “TSBWH”
Yes | Alarm level | HH | High-high condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “1100”. Alarm becomes active if signal > 1100 | Hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 1100. Alarm (HH) wordt dan actief bij waarde > 1100
Yes |  | H | High condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “1000”. Alarm becomes active if signal > 1000 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 1000. Alarm (H) wordt dan actief bij waarde > 1000
Yes |  | L | Low condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “600”. Alarm becomes active if signal < 600 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 600. Alarm (H) wordt dan actief bij waarde < 600
Yes |  | LL | Low-low condition setpoint (value in units of signal Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “500”. Alarm becomes active if signal < 500 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 500. Alarm (H) wordt dan actief bij waarde < 500
Yes |  | F | Setpoint for fault condition of binary I/O: “True” (for active) or “False” (for inactive). Therefore whetthe setpoint is "False" and the actual signal becomes inactive, the alarm will become active after the on delay time [Delay on] | Setpoint voor fout conditie van binaire I/O: "True" (voor actief) en "False" (voor inactief). Dus als setpoint is "False" en het signaal wordt inactief (NC), dan gaat wordt het alarm actief na het verstrijken van de off delay [Delay on]
Yes | Alert Code |  | Unique alert code, not as key for this list, but mandatory for a alarm definition | Deze unieke alert code is ontstaan om ondubbelzinnig over een alarm te kunnen communiceren en is alleen verplicht voor alarmen.
No | Cabinet |  | Cabinet number or name for selection filtering, not mandatory, therefore the syntax will not be checked. (This text will also be displayed in I/O list on screen) | Cabinet naam of nummer is hier in te vullen, deze gegevens kunnen voor selectiefilters worden gebruikt en wordt vermeld in het I/O lijst, maar er is geen invulverplichting.
No | Cable Core No |  | Core number isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Core No. (ader nummer) is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Cable ID |  | Cable id isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Cable ID is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Cable Type |  | Cable type isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Cable Type is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Call GEA on Alert |  | Automatically trigger a GEA when this alert becomes active | Veroorzaak een GEA als dit alarm actief wordt
Yes | Data Type |  | Type of data, Valid data types are: | Date type, valide types zijn:
|  |  | - Boolean: “Bool” | - Booleon: "Bool"
|  |  | - 16 bits word: “Word16” | - 16 bits word: “Word16”
|  |  | - Signed 16 bits integer: “Int16” | - Signed 16 bits integer: “Int16”
|  |  | - Unsigned 16 bits integer: “UInt16” | - Unsigned 16 bits integer: “UInt16”
|  |  | - Signed 32 bits integer: “Int32” | - Signed 32 bits integer: “Int32”
|  |  | - Unsigned 32 bits integer: “UInt32” | - Unsigned 32 bits integer: “UInt32”
|  |  | - Signed 64 bits integer: “Int64” | - Signed 64 bits integer: “Int64”
|  |  | - Floating point number: “Float” | - Floating point number: “Float”
|  |  | - Date and time: “DateTime” | - Date and time: “DateTime”
|  |  | - String of ASCII chars: “AsciiString(N)” (where N is the number of characters in the string.) | - String van ASCII chars: “AsciiString(N)” (N is het aantal karakters in de string.)
|  |  | DateTime should be a 32-bit word that counts the number of seconds since 1970-01-01T00:00:00Z. | DateTime moet een 32--bit word zijn de het aantal seconden telt vanaf 1970-01-01T00:00:00Z
|  |  | Hardwired DI and DO type signals are Bool; AI and AO are UInt16 | Bekabelde DI en DO signalen zijn van het type Boolean, AI en AO zijn Uint16
Yes | Delay On |  | Delay time for activating the alert, e.g. for 4 seconds delay: “4” | Inschakel vertraging voor het alarm in seconden, b.v. 4 sec vertraging: "4"
Yes | Deleted |  | Row has been deleted and should be ignored (mark with revision letter when row was deleted). | Deze rij is verwijderd en wordt genegeerd, maar blijft staan vanwege revisiebeheer of het is van tijdelijke aard.
Yes | Description |  | Description of signal, this tekst is also used as an alarm description, e.g. "Common alarm valve system" | Beschrijving van het signaal, deze tekst wordt ook gebruikt als alarmtext, e.g. "Algemeen alarm kleppen besturing"
Yes | Device |  | Unique identifier for device providing the IO. For example; | De unieke devicenaam waar het item bij hoort, bijvoorbeeld;
|  |  | - Hardwired:: PLC OID -> "70UP100" | - Bedraad: PLC OID -> "70UP100"
|  |  | - Serial with gateway (MB/RTU -> MB/TCP): Gateway OID -> "GW1" | - Serieel middels een gateway (MB/RTU -> MB/TCP): Gateway OID -> "GW1"
|  |  | - Serial directly to PLC comm. Kaart: PLC OID -> "70UP100" | - Serieel middels een PLC comm. Kaart: PLC OID -> "70UP100"
|  |  | - Modbus TCP/IP: MB-device OID -> "MainEngine" | - Modbus TCP/IP: MB-device OID -> "MainEngine"
Yes | Disallow Inhibit |  | Do not allow alert to be inhibited, when marked with an “X” | Sta niet toe dat dit item ge-inhibit kan worden. Gebruik bij voorkeur een "X" om aan te geven dat deze optie actief is.
No | Do Not Export |  | When not empty, item will not be exported into Codesys export files for wago | Als dit veld niet leeg is, zal dit item niet worden meegenomen in de export files voor codesys, dit veld is voorlopig specifiek voor wago plc's
No | Do Not Log |  | When not empty, item will not be logged when using datalogging | Als dit veld niet leeg is, zal dit item niet worden meegenomen in de datalogging,
No | Log to Daily Report |  | Include this I/O in the engine room report | Gebruik dit I/O in het engine room report.
Yes | General Lock[3] Tag | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | Group Alarm |  | Resound alert if input is toggled, despite being silenced. If the alarm signal is meant as a common or groupalarm, this alert can be setup to resound the it alarm horn then alarmlevel is toggled. | Opnieuw de alarm hoorn activeren als de alarm ingang opnieuw geactiveerd wordt, ondankt dat de hoorn voor dit alarm is afgezet. Als het item bedoeld is als een groepsalarm, dan kan dit alart worden ingesteld als groupsalarm, waardoor de hoorn opnieuw kan afgaan bij verandering van de ingang.
Yes | H Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | HH Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | I/O type |  | Type of I/O: | I/O type:
|  |  | - Digital input: “DI” | - Digitale input: "DI"
|  |  | - Digital output: “DO” | - Digitale output: "DI"
|  |  | - Analog input (also PT100): “AI” | - Analoge input: "AI"
|  |  | - Analog output: “AO” | - Analoge output: "AO"
|  |  | - Serial io: “SE” | - Seriële I/O: "SE"
Yes | Intended Operator Response |  | Field to provide extra information and to provide some pointers about the cause and probable solutions to fix the cause of this alert. This is a new mandatory column expected by class. For now class expects as a minimal effort to direct the operator to the operator manual. | Dit veld is bedoeld om extra informate en tips te geven omtrend dit alarm (b.v. een samenvatting uit de handleiding zijn) om de alarm situatie adequaat op te kunnen lossen. Dit is een relatief nieuwe kolom waarbij klasse in eerste in stantie minimaal een verwijzing naar het handboek verwacht.
Yes | L Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | LL Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | Modbus address |  | Modbus address for the I/O (format <word address>.<bit nr> or <bit address> in decimals) | Modbus address voor de I/O in het volgende formaat <word address>.<bit nr> or <bitaddress> allen in decimalen
Yes | Modbus function codes |  | Allowed Modbus functions at this Modbus address. Separate by comma when multiple codes are allowed. (Modbus protocol only) for modbus codes. | Modbus function code voor dit address, Als er meerdere functiecodes zijn toegestaan dan kun je die hier gescheiden door komma's invullen
Yes | Modbus slave address |  | Modbus slave address for external device. Mandatory for modbus signals | Modbus slave adres voor devices die via modbus communiceren, in dat geval it het een verplicht veld
Yes | Module |  | Device module where the IO is connected (not used for serial interface that are not connected to a [Device]) [2]. | Device module waarop het item is aangesloten. In het geval van een PLC bedoelen we de I/O kaart OID -> "DI1", deze kolom wordt niet gebruikt bij seriële signalen.
|  |  | For example: | Bijvoorbeeld:
|  |  | - The first Digital input card: “DI1” | - De eerst digitale ingangskaart: "DI1"
|  |  | - The second analog output card: “AO2” | - De tweede analoge outgangskaart: "AO2"
|  |  | - Can also be used to indicate switch OID for TCP/IP signals, e.g. "7U2" | - Kan bij TCP-IP verbindingen worden gebruikt om het switch OID aan te geven, b.v. "7U2"
Yes | OPC UA | Node ID | The unique identifier for a node in an OPC server’s address space | Het unique id voor de node dat bij dit signaal hoort in een OPC server zijn address space
Yes | OPC UA | Publish Interval | The publishi interval (in ms) is the cycle time at which a subscription executes | De publish interval is de tijd wanneer een subscription wordt uitgevoerd
No | P&ID |  | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht
Yes | Priority |  | Alarm priority type: “alarm”, “emergency”, “warning”, “caution” or empty (if unsure, use “alarm”), mandatory if item is an alarm. | Alarm prioriteit, we onderscheiden de volgende types: “alarm”, “emergency”, “warning”, “caution” of leeg laten bij geen alarm (als je het niet zeker weet, neem dan standaard “alarm”. Deze kolom is verplicht voor alarmen.
Yes | Range | Lower | Lower value of range. (Mandatory for analog signals) | Laagste waarde van de school (verplicht voor analoge signalen)
Yes |  | Upper | Upper value of range. (Mandatory for analog signals) | Hoogste waarde van de school (verplicht voor analoge signalen)
Yes | Rev |  | Last revision when the row has changed. | Revisie van de laatste wijziging
Yes | Sounding Locations |  | Additional locations where alarm buzzer should be activated, using the same location names as the acknowledge location, e.g. “WH,ECR,ERPS”. This option doen's affect the way alarms are displayed, all alarms are displayed on every workstation, bus by using samrt sorting techniques, sorting is based upon location, alert priority and timestamp. Alarms from other locations can be found further down the active alarm list or on top if there are no alarms for this location. | Additionele locaties waar de alarm hoorn ook af moet gaan als het alarm actief word, hierbij worden dezelfde locatie namen gebruikt als bij de kolom [Acknowledge location], locaties worden dan door komma's geschieden, b.v.; "WH,ECR,ERPS". Deze optie heeft niets te maken met het tonen van alarmen. Alle alarmen worden op alle workstations getoond, maar door slimme sorteermethodes worden de alarmen gesorteerd wordt op locatie, alert prioriteit en tijdsstempel.
Yes | System |  | Used for sorting by system, when using this column, system grouping can be used, for instance in the I/O maintenance screen. Intended to be a short description e.g. "ME PS" or "FAS" or "TMS". Max 16 characters. | Wordt gebruikt voor het sorteren van de items, bijvoorbeeld in het I/O lijst scherm onder maintenance. Bedoeld als korte omschrijving, bijv. "ME PS" of "FAS" of "TMS". Max 16 karacters.
Yes | Tag |  | Unique IO identifier (Composed of an SFI code and an abbreviation for the function) | Uniek id voor dit signaal, dit mag een SFI codering zijn of in de meeste gevallen iets beschrijvends, zoals "CommonAlarm"
Yes | Is Subscribe |  | Define if the line is a subscribe to another Tag in the I/O List. | Specificeert of the lijn “subscribed” op een andere lijn in de I/O lijst
Yes | Prefix Device |  | The tag will be published in our system with the device as a prefix | De tag wordt gepubliseerd met de devicenaam als voorvoegsel in ons systeem
Yes | Terminal |  | To further specify the signals connected to the [Module], use the input number of the i/o module mentioned in column [Module], e.g. third input on DI: “3” | Deze kolom is bedoeld ter aanvulling van de kolom [Module], hier geef je aan op welke in- of uitgang van de [Module] het signaal is aangesloten, b.v. derde input op DI2: "3"
|  |  | For serial interfaces: | Voor seriële interfaces:
|  |  | - With gateway: Port number on gateway e.g. "2" | - Bij gebruik van een Gateway: Poortnummer op gateway, b.v. "2"
|  |  | - Directly to PLC: not used | - Direct op een [Device] zonder module, b.v. "X2"
|  |  | - Modbus TCP/IP: Port number on switch, e.g. "3" | - Kan bij TCP/IP verbindingen worden gebruikt voor poortnummer op switch, b.v. "1"
No | Timestamp |  | Workstation of last change in io item | Geeft aan op welk werkstation de laatste wijziging is gedaan
Yes | Unit |  | Unit of the measured value. For example; Bar, mA | Eenheid van het te meten signaal. Bijvoorbeeld Bar, mA, wordt o.a. gebruikt voor trending
Yes | VDR ID |  | Send all changes to voyage data recorder. Mark with unique ID number, which will also be send to the VDR system. Leaving the column empty means, VDR notification is not applicable | Middels deze kolom is aan te geven of het alarm doorgezet moet worden naar het VDR systeem, waar van toepassing. Als deze kolom niet leeg is, is het doorsturen van toepassing. Gebruik bij voorkeur een unit id nummer welke meegezonden wordt naar de VDR.
No | Workstation |  | Do not used, colums is used by system to indicate workstation of last change in io item | Niet gebruiken, deze kolom wordt door het systeem gebruikt om aan te geven op welk werkstation de laatste wijziging is gedaan
No | Yard Tag |  | Informative item for separated Yard id numbering or e.g. for SFI coding | Informatief veld voor b.v. aparte werfcondering of SFI codering.
Additional columns are allowed, if the column is not defined in the list above, it will be ignored. Examples are; - Green line (level for green line on gauge to indicate nominal value) - Red line (for max level) - Specific ID's - Extended cabinet name / location - Eplan coding - Prefix - etc. |  |  |  | Meer kolommen toevoegen voor meer detailering / extra informatie of kruisverwijzingen is geen probleem, onbekende kolommen worden genegeerd. Bijvoorbeeld; - Green line (nominale niveau die met een groene lijn op een meter wordt aangegeven) - Red line (max niveau die je aan aangeven met een rode lijn) - Kruisverwijzingen / ID's - Uitgebreidere omschrijvingen van panelen en locaties - Prefix - etc.
[1] Mandatory columns can be empty, but they have to be defined in the I/O list

## Internal lists
Direction | Data Type | Alert Priority | Lock Operator | True False | Modbus Data Type | Module Type
In | Bool | Emergency | < | True | Coil | ReadFieldbus
InOut | Int16 | Alarm | > | False | Input | WriteFieldbus
Out | Int32 | Warning | = |  | InputRegister | ReadWriteFieldbus
| Int64 | Caution |  |  | HoldingRegister | RetainPersistent
| UInt16 | Event |  |  |  | Other
| UInt32 |  |  |  |  | 750-403
| UInt64 |  |  |  |  | 750-430
| Float |  |  |  |  | 750-454
| Double |  |  |  |  | 750-455
| DateTime |  |  |  |  | 750-461
| TimeSpan |  |  |  |  | 750-461/000-003
| UnixDateTime |  |  |  |  | 750-464#02-RTD-PT
| String |  |  |  |  | 750-485
| AsciiString |  |  |  |  | 750-511/000-001
| IpAddress |  |  |  |  | 750-511/000-002
| Blob |  |  |  |  | 750-517
750-530
750-554
750-555
750-610
750-1400
750-1415
750-1425
750-1500
750-1515