## Rev
Revision | Description / Remarks
R0.0 | Initial release from template for Project Zero
R0.1 | IO-list according single line version R1.5 - dd 2023-11-14
R0.2 | Re-arranged columns acc. standard. - dd. 2023-11-22 Essential IO (Internal) transferred to PMS Io-list (UMS entrance, acc. Alarm panels) dd. 2023-11-24 Update acc. comments yard - dd. 2023-11-21
R0.3 | Adjusted to latest System Overview R1.6. (ASI interface moved from AMCS KEB3 to PMS IO list KEB4) - dd 2023-12-01
R0.4 | Adjusted to the latest System Overview R1.7. Deleted KEB 3 in the main saloon. - dd. 2024-02-07 Also moved internal IO from KEB3 to KEB2 for "Bridge" silence and buzzer connection
R1.0 | Added Alewijnse AC board IO (Pump control) dd. 5-03-2023
R1.1 | Name of the list adjusted to the detailed engineering project number - dd 04-04-2024 Adjusted the IO-locations of the water sensors to CB.02 - dd 04-04-2024 Changed system numbers BUMO to the yard system numbers 05-04-2024 Added fresh water system 05-04-2024
R1.2 | Added Tijssen Monitor Switching per location. 16-04-2024
R1.3 | Final Bilge & Fifi info based on Multinlines Alewijnse 2-05-2024 Added DE and Nde Pt100 readouts of propulsion motors (16-05-2024)
R1.4 | Added internal IO
R1.5 | Added Accelleration sensors 1x MTS & 1x Crew. (3-06-2024) Hull temperature Activation output added in CB.01 (04-06-2024) Added pneumatic prseeure sensor (11-06-2024)
R1.6 | IO card rename
R1.7 | Added Grey & Black Water System (04-07-2024) Changed the 750-461 pt100 cards to 750-450#2 cards in consultancy with Wouter. Added Deck Equipment Deck Crane inputs (04-07-2024)
R1.8 | Updated project to latest release, updated IO list to work with latest release and minimize validation failures in software
R1.9 | Wago 750-450 card update
R1.10 | Added "Sideboarding platform crew (PS) Closed & Locked" for Doors & hatches system - dd 08-10-2024 Added fire detection fault input dd 11-10-2024 Added KEB1 DO61 output card dd 15-10-2024 Battery Ventilation IO added dd 15-10-2024 Watertight hinged doors IO added dd 17-10-2024 Added KEB1 DO62 output card for Locker, FP & Laz Ventilation dd 28-10-2024 Added KEB1 DI30 4-20mA input card dd 29-10-2024
R1.11 | Added IO for Fire Dampers MTS Ventilation dd.4-11-2024 Added SOS locker in and outputs for bilge & Fifi system dd. 12-11-2024 Updeted Tags formulas for validation 14-11-2024 Added Input in Prefix Device kolom for valication. 14-11-2024
R1.12 | Novec Inputs added according latest info. Dd 2024-11-29
R1.13 | Monitoren IO update according latest POD layout and KVM updates dd 9-12-2024.
R1.13_FAT | IO-list confirm the production drawings R2.0 to perform the FAT (Changes in Blue). - dd 14-01-2024
R1.14_FAT | KEB1 AI34 and KEB1 DO62 removed for FAT, added module 750-626/020-002 (earth fauld detection) Removed Alarm on KEB1 DI00.2 & KEB1 DI00.2, these are spares now. KEB1 AI30 -> needs to be changed from 750-450 to 750-455. Alarm settings Bilge Alarms changed. -> Changed to Emergency and souning on BRG location Also all alarm inputs set to alarming and Fail inputs too.
R2.0 | *** Conversion version *** KEB1 AI30 -> 750-455 Kaart moet besteld worden en in Eplan van Type wijzigen. KEB1 AI33 & AI34 delete from de PLC Train KEB1 SE1_DMX -> Deleted KEB1 DO62 750-1500 toevoegen in Eplan en bestellen KEC1_P1 Verwijderd KEC1_P2 Verwijderd KEC1_P3 Verwijderd KEC1_P4 Verwijderd KEB2 AI32 & AI33 delete from de PLC Train KEC2_P1 Verwijderd KEC2_P2 Verwijderd KEC2_P3 Verwijderd KEC2_P4 Verwijderd KEC3_P1 Verwijderd KEC3_P2 Verwijderd KEC3_P3 Verwijderd KEC3_P4 Verwijderd KEB1 DI37, DI38 & DI39 verwijderd. KEB2 DI37, DI38 & DI39 verwijderd.
R2.1 | Added Monitor Source Toggle inputs for Mission Room, Ships Office, Crew mess & Captains screens. Moved PS mouse toggle from CB2 to CB1. Moved Mouse & PS Helm Monitor controls from CB2 to CB1. Added 24Vdc alarms 14E01 from Alewijnse mutilines. Added fire flap Hood 2 Added PCS Alarms in KEB1 & KEB2 MQTT kolommen added & OPC_UA kolommen deleted.
R2.2
R2.3 | Added all cables according Alewijnse Wk11 revision and Eplan so far. Added Sea water cooling pumps.
R2.4 | PS Boarding Platform Closed and locked cable added. See mail AB dd 07-04-2025 Fire Sliding Door Galley Crew Mess added, see mail AB dd 1-04-2025 Owners Deckhouse Sliding Window added dd 11-04-2025 Added Petrol sensors 1x DI & 1x AI in Keb2 dd17-04-2025 Mqtt topics added for IO in the columns added dd 24-04-2025
R2.5 | Fresh Water system revision dd 2025-05-19
R2.6 | Power tags added as per info received dd. 2025-05-22 AB Added Butterfly valves HVAC Ventilation Supply CB.02 4xDI.

## Project definitions
Devices | Cabinet | Systems | Locations
PHW1 | 70.51 Alarm Cabinet WH | AMCS | BRG
PHW2 | 70.52 Alarm Cabinet TS | EMS | ER
PHW3 | 70.53 Alarm Cabinet ER | BMS | TS
PHU1 |  | PCS
PHU2 |  | HEALTH
KEB1 |  | PAT
KEB2 |  | TMS
KEB3 |  | Modbus
KEB4 |  | VPS
KEB5
KEF1 |  | 0900 DOORS HATCHES
KEF2 |  | 1500 PROPULSION
BRG |  | 1500 LUBE OIL
ER |  | 1700 STEERING GEAR
TS |  | 2100 BILGE FIFI
Health |  | 2100 GENERAL SERVICE
UAP |  | 2200 UNDERWATER LIGHTS
VIRT-KFE1 |  | 2500 FRESH WATER
VIRT-KFE2 |  | 2500 GREY WATER
VIRT-PHW |  | 2700 DOMESTIC EQUIPM
TMS |  | 2800 HYDRAULIC
SoftPLC |  | 2900 PNEUMATIC
NAVLIGHTS |  | 3000 DIRTY OIL
Alarming |  | 3400 SEWAGE
PHU3 |  | 3500 VENTILATION
SystemHealthMonitor |  | 3500 FIREDAMPER
WagoPlcAdapter |  | 3800 SEAWATER
UapServer |  | 4100 COOLING WATER
MdbsSrvTst |  | 4500 CCTV
MdbsClntTst |  | 4500 DYNAMIC CONV
4500 UGRID
4500 24VDC SYSTEM
4500 AMCS
7500 WINCHES
7500 DECK CRANE
7500 PASSERELLE
7500 BOARDING LADDER

## IO-List
Rev. | Deleted | Target Type | Device | Module | Module Type | Terminal | Is Subscribe | Prefix Device | Tag | Cabinet | OPC UA |  | System | Yard Tag | Description | Parent | Redundant tag | P&ID | Cable |  |  | Mqtt |  |  | Modbus | [7 empty] | Range |  | Unit | Precision | Alert Code | Alert |  |  |  |  | Delay On | Acknowledge Location | Sounding Locations | Alert priority | Intended Operator Response | Category A | Group Alarm | Call GEA on Alert | Disallow Inhibit | Vdr ID | General Lock |  |  | HH Lock |  |  | H Lock |  |  | L Lock |  |  | LL Lock |  |  | Do Not Log | Log To Daily Report | Log to CDP | Workstation | Timestamp
[11 empty] | Node ID | Publish Interval | [6 empty] | ID | Type | Core No. | Device | Topic | Json Path | Slave Address | Data Type | Address | Source Type | Byte Size | Swap Words | Lower | Upper | Lower | Upper |  |  |  | HH | H | L | LL | F | [10 empty] | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level
| True | [13 empty] | ALARM CABINET - AMCS Main technical Space +CB.1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 0 |  | True | GFDEnabled | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Ground Fault Diagnostics Enabled | [6 empty] | Mqtt1 | 450000 AMCS | $.GFDEnabled
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 2 |  | True | FieldVoltageAvailable | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Voltage Available | [6 empty] | Mqtt1 | 450000 AMCS | $.FieldVoltageAvailable
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 4 |  | True | PA24V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Pre-Alarm 24V | [6 empty] | Mqtt1 | 450000 AMCS | $.PA24V | [12 empty] | 6 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 5 |  | True | MA24V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Main-Alarm 24V | [6 empty] | Mqtt1 | 450000 AMCS | $.MA24V | [12 empty] | 7 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 6 |  | True | PA0V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Pre-Alarm 0V | [6 empty] | Mqtt1 | 450000 AMCS | $.PA0V | [12 empty] | 8 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB1 | R1 | 750-626/020-002 | 7 |  | True | MA0V | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Distribution Insulation Main-Alarm 0V | [6 empty] | Mqtt1 | 450000 AMCS | $.MA0V | [12 empty] | 9 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI00 | 750-1415 | 1 |  | True | AmcsPowerSupplyFailure | DSK_SWR |  | 1000 | 450000 AMCS |  | MTS AMCS KEB1 Power Supply Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPowerSupplyFailure | [12 empty] | 10 |  |  |  |  | False |  | TS |  | Alarm | Check Primary (G2) supply, Secundary (G3) supply and redundancy module (G1) |  |  |  |  | 1
R1.9 |  | Bool | KEB1 | DI00 | 750-1415 | 2 |  | True | Spare_DI00_2 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 3 |  | True | UmsEntranceUnitMannedSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit Manned Switch | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsEntranceUnitMannedSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 4 |  | True | UmsEntranceUnitUnmannedSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit Unmanned Switch | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsEntranceUnitUnmannedSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 5 |  | True | UmsEntranceUnitOneManSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit One Man Switch | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsEntranceUnitOneManSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 6 |  | True | UmsEntranceUnitMoreMenSwitch | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Entrance Unit More Men Switch | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsEntranceUnitMoreMenSwitch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 7 |  | True | UmsOneManTimerResetButton | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS One Man Timer Reset Button | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsOneManTimerResetButton
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 8 |  | True | Spare_DI00_8 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 1 |  | True | AlarmPanelSilenceButton | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Silence Button | [6 empty] | Mqtt1 | 450000 AMCS | $.AlarmPanelSilenceButton
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 2 |  | True | Spare_DI01_2 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 3 |  | True | AlarmPanelGeaCallRevokeButton | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel GEA CallRevoke Button | [6 empty] | Mqtt1 | 450000 AMCS | $.AlarmPanelGeaCallRevokeButton
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 4 |  | True | AlarmPanelAcknowledgeButton | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Acknowledge Button | [6 empty] | Mqtt1 | 450000 AMCS | $.AlarmPanelAcknowledgeButton
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 5 |  | True | Spare_DI01_5 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 6 |  | True | Spare_DI01_6 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 7 |  | True | Spare_DI01_7 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 8 |  | True | Spare_DI01_8 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 1 |  | True | UmsMannedLight | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Manned Light | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsMannedLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 2 |  | True | UmsTimingOnLight | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS Timing On Light | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsTimingOnLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 3 |  | True | Spare_DO00_3 | DSK_SWR |  | 1000 | SPARE |  | Spare
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 4 |  | True | UmsOneManTimerResetLight | DSK_SWR |  | 1000 | 450000 AMCS |  | UMS One Man Timer Reset Light | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsOneManTimerResetLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 5 |  | True | AlarmPanelSilenceLight | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Silence Light | [6 empty] | Mqtt1 | 450000 AMCS | $.AlarmPanelSilenceLight
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 6 |  | True | AlarmPanelGeaCallRevokeLight | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel GEA CallRevoke Light | [6 empty] | Mqtt1 | 450000 AMCS | $.AlarmPanelGeaCallRevokeLight
R1.9 |  | Bool | KEB1 | DO00 | 750-1515 | 7 |  | True | MachinerySpaceBuzzerHorn | DSK_SWR |  | 1000 | 450000 AMCS |  | Machinery Space Buzzer Horn | [6 empty] | Mqtt1 | 450000 AMCS | $.MachinerySpaceBuzzerHorn
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 8 |  | True | AlarmPanelAcknowledgeLight | DSK_SWR |  | 1000 | 450000 AMCS |  | Alarm Panel Acknowledge Light | [6 empty] | Mqtt1 | 450000 AMCS | $.AlarmPanelAcknowledgeLight
R1.8 |  | Bool | KEB1 | F1 | 750-610 | 1 |  | True | AmcsPlcPowerModule1InternalFuseBlown | DSK_SWR |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 1 Internal Fuse Blown | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule1InternalFuseBlown | [12 empty] | 34 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | F1 | 750-610 | 2 |  | True | AmcsPlcPowerModule1PowerFailure | DSK_SWR |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 1 Power Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule1PowerFailure | [12 empty] | 35 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI20 | 750-1415 | 1 |  | True | BILGE_LEVEL_SUB_PUMP1_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001048_1 | WATER SENSOR Submersible Pump 1 41001048_1 |  |  |  | 601W0004.3 | 14x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_LEVEL_SUB_PUMP1_ALARM | [12 empty] | 36 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI20 | 750-1415 | 2 |  | True | BILGE_LEVEL_SUB_PUMP2_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001048_2 | WATER SENSOR Submersible Pump 2 41001048_2 |  |  |  | 601W0004.3 |  |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_LEVEL_SUB_PUMP2_ALARM | [12 empty] | 37 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI20 | 750-1415 | 3 |  | True | BILGE_LEVEL_SUB_PUMP3_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001048_3 | WATER SENSOR Submersible Pump 3 41001048_3 |  |  |  | 601W0004.3 |  |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_LEVEL_SUB_PUMP3_ALARM | [12 empty] | 38 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 4 |  | True | GEN_SERV_PUMP1_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001001 | General Service Pump 1 Remote Available |  |  |  | 381W0005 | 2x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.GEN_SERV_PUMP1_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 5 |  | True | GEN_SERV_PUMP2_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001002 | General Service Pump 2 Remote Available |  |  |  | 381W0004 | 2x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.GEN_SERV_PUMP2_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 6 |  | True | GEN_SERV_PUMP2_FIELD_START | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | General Service Pump 2 Field Start |  |  |  | 381W0003 | 7x1,5 |  | Mqtt1 | 210000 BILGE FIFI | $.GEN_SERV_PUMP2_FIELD_START
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 7 |  | True | GEN_SERV_PUMP2_FIELD_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | General Service Pump 2 Field Stop | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.GEN_SERV_PUMP2_FIELD_STOP
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 8 |  | True | STRIP_PUMP_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001004 | Stripping Pump Remote Available |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 | 210000 BILGE FIFI | $.STRIP_PUMP_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 1 |  | True | STRIP_PUMP_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Stripping Pump Running | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.STRIP_PUMP_RUNNING
R2.2 |  | Bool | KEB1 | DI21 | 750-1415 | 2 |  | True | Spare_DI21_2 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 3 |  | True | CHAIN_LOCK_PUMP_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001005 | Chain Locker Pump Remote Available |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 | 210000 BILGE FIFI | $.CHAIN_LOCK_PUMP_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 4 |  | True | CHAIN_LOCK_PUMP_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Chain Locker Pump Running | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.CHAIN_LOCK_PUMP_RUNNING
R2.2 |  | Bool | KEB1 | DI21 | 750-1415 | 5 |  | True | Spare_DI21_5 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 6 |  | True | SUBMERS_PUMP1_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006-1 | Submersible Pump 1 Remote Available |  |  |  | 381W0009 | 7x2x0.75 |  | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP1_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 7 |  | True | SUBMERS_PUMP1_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Submersible Pump 1 Running | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP1_RUNNING
R1.3 |  | Bool | KEB1 | DI21 | 750-1415 | 8 |  | True | Spare_DI21_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 1 |  | True | SUBMERS_PUMP2_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006-2 | Submersible Pump 2 Remote Available |  |  |  | 381W0085 | 4x2x0.75 |  | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP2_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 2 |  | True | SUBMERS_PUMP2_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Submersible Pump 2 Running | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP2_RUNNING
R1.3 |  | Bool | KEB1 | DI22 | 750-1415 | 3 |  | True | Spare_DI22_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 4 |  | True | SUBMERS_PUMP3_REM_AVAIL | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_3 | Submersible Pump 3 Remote Available |  |  |  | 381W0009 | 7x2x0.75 |  | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP3_REM_AVAIL
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 5 |  | True | SUBMERS_PUMP3_RUNNING | +CB.1 |  | 1000 | 210000 BILGE FIFI |  | Submersible Pump 3 Running | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP3_RUNNING
R1.3 |  | Bool | KEB1 | DI22 | 750-1415 | 6 |  | True | Spare_DI22_6 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R1.8 |  | Bool | KEB1 | DI22 | 750-1415 | 7 |  | True | FRESH_WATER_MAK1_ALARM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001001_1 | Fresh Water Maker 1 Common Alarm |  |  |  | 421.1W0003 | 4x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.FRESH_WATER_MAK1_ALARM | [12 empty] | 58 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI22 | 750-1415 | 8 |  | True | FRESH_WATER_MAK2_ALARM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001001_2 | Fresh Water Maker 2 Common Alarm |  |  |  | 421.1W0006 | 4x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.FRESH_WATER_MAK2_ALARM | [12 empty] | 59 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI23 | 750-1415 | 1 |  | True | FRESH_WATER_CHLORINE_UNIT_ALARM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001017 | Chlorine Dosing Unit Common Alarm |  |  |  | 421.1W0010 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.FRESH_WATER_CHLORINE_UNIT_ALARM | [12 empty] | 60 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 2 |  | True | TRANS_PUMP_BLCK_WAT_REM_AVAIL | +CB.1 |  | 1000 | 340000 SEWAGE | 34001001 | Transfer Pump 2 Blackwater Remote Available |  |  |  | 447W0004 | 7x2x0.75 |  | Mqtt1 | 340000 SEWAGE | $.TRANS_PUMP_BLCK_WAT_REM_AVAIL
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 3 |  | True | TRANS_PUMP_BLCK_WAT_RUNNING | +CB.1 |  | 1000 | 340000 SEWAGE |  | Transfer Pump 2 Blackwater Running | [6 empty] | Mqtt1 | 340000 SEWAGE | $.TRANS_PUMP_BLCK_WAT_RUNNING
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 4 |  | True | TRANS_PUMP_GREY_WAT_REM_AVAIL | +CB.1 |  | 1000 | 340000 SEWAGE | 34001002 | Transfer Pump 1 Greywater Remote Available |  |  |  | 447W0007 | 7x1,5 |  | Mqtt1 | 340000 SEWAGE | $.TRANS_PUMP_GREY_WAT_REM_AVAIL
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 5 |  | True | TRANS_PUMP_GREY_WAT_RUNNING | +CB.1 |  | 1000 | 340000 SEWAGE |  | Transfer Pump 1 Greywater Running | [6 empty] | Mqtt1 | 340000 SEWAGE | $.TRANS_PUMP_GREY_WAT_RUNNING
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 6 |  | True | PUMP_FWD_GREY_WAT_REM_AVAIL | +CB.1 |  | 1000 | 340000 SEWAGE | 34001003 | Pump 3 Fwd Grey Water Remote Available |  |  |  | 447W0004 | 7x2x0.75 |  | Mqtt1 | 340000 SEWAGE | $.PUMP_FWD_GREY_WAT_REM_AVAIL
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 7 |  | True | PUMP_FWD_GREY_WAT_RUNNING | +CB.1 |  | 1000 | 340000 SEWAGE |  | Pump 3 Fwd Grey Water Running | [6 empty] | Mqtt1 | 340000 SEWAGE | $.PUMP_FWD_GREY_WAT_RUNNING
R2.5 |  | Bool | KEB1 | DI23 | 750-1415 | 8 |  | True | FRESH_WATER_CIRC_PUMP_RUNNING | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001150 | Fresh Water Circulation Pump Running |  |  |  | 421.1W0172 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.FRESH_WATER_CIRC_PUMP_RUNNING
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 1 |  | True | SEW_TREAT_RELEASE | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant Release |  |  |  | 447W0024 | 7x2x0,75 |  | Mqtt1 | 340000 SEWAGE | $.SEW_TREAT_RELEASE
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 2 |  | True | SEW_TREAT_GEN_WARNING_ALARM | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant General Warning Alarm | [6 empty] | Mqtt1 | 340000 SEWAGE | $.SEW_TREAT_GEN_WARNING_ALARM | [12 empty] | 69 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.5 |  | Bool | KEB1 | DI24 | 750-1415 | 3 |  | True | Sewage_Treatment_Plant_General_Alarm | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant General Alarm | [6 empty] | Mqtt1 | 340000 SEWAGE | $.Sewage_Treatment_Plant_General_Alarm
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 4 |  | True | SEW_TREAT_DRY_RUNN_PROT | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant Dry Running Protection & Cleaning Pump |  |  |  | 447W0024 | 7x2x0,75 |  | Mqtt1 | 340000 SEWAGE | $.SEW_TREAT_DRY_RUNN_PROT
R2.2 |  | Bool | KEB1 | DI24 | 750-1415 | 5 |  | True | PASS_HATCH_CL_LOCK | +CB.1 |  | 1000 | 750000 DECK EQUIP |  | Passerelle Hatch Closed & Locked |  |  |  | 601W0005.2 | 14x2x0.75 |  | Mqtt1 | 750000 DECK EQUIP | $.PASS_HATCH_CL_LOCK
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 6 |  | True | SBL_SB_CLOSED_LOCKED | +CB.1 |  | 1000 | 750000 DECK EQUIP |  | SB Side Boarding Ladder Closed & Locked |  |  |  | 543W0002 | 4x2x0,75 |  | Mqtt1 | 750000 DECK EQUIP | $.SBL_SB_CLOSED_LOCKED
R2.2 |  | Bool | KEB1 | DI24 | 750-1415 | 7 |  | True | SBL_COMMON_ALARM | +CB.1 |  | 1000 | 750000 DECK EQUIP |  | Side Boarding Ladder Common Alarm | [6 empty] | Mqtt1 | 750000 DECK EQUIP | $.SBL_COMMON_ALARM | [12 empty] | 74 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.5 |  | Bool | KEB1 | DI24 | 750-1415 | 8 |  | True | Sewage_Treatment_Plant_On | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant On | [6 empty] | Mqtt1 | 340000 SEWAGE | $.Sewage_Treatment_Plant_On
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 1 |  | True | TECH_CORRIDOR_ESC_HATCH_SB | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Technical Corridor Escape Hatch SB Nr.27 |  |  |  | 535W0016 | 2x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.TECH_CORRIDOR_ESC_HATCH_SB
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 2 |  | True | TECH_ROOM_ESC_HATCH_PS | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Technical Room Escape Hatch PS Nr.31 |  |  |  | 601W0004.3 | 14x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.TECH_ROOM_ESC_HATCH_PS
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 3 |  | True | MAIN_DECKH_VENT_HATCH_SB | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch SB Nr.33 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.MAIN_DECKH_VENT_HATCH_SB
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 4 |  | True | MAIN_DECKH_VENT_HATCH_PS | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch PS Nr.34 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.MAIN_DECKH_VENT_HATCH_PS
R2.4 |  | Bool | KEB1 | DI25 | 750-1415 | 5 |  | True | Spare_DI25_5 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.4 |  | Bool | KEB1 | DI25 | 750-1415 | 6 |  | True | Spare_DI25_6 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 7 |  | True | LAZA_ACCESS_HATCH_SB_FWD | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch SB Fwd Nr.37 |  |  |  | 601W0005 | 19x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.LAZA_ACCESS_HATCH_SB_FWD
R2.2 |  | Bool | KEB1 | DI25 | 750-1415 | 8 |  | True | LAZA_ACCESS_HATCH_PS_FWD | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch PS Fwd Nr.38 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.LAZA_ACCESS_HATCH_PS_FWD
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 1 |  | True | LAZA_ACCESS_HATCH_SB_MID | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch SB Mid Nr.39 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.LAZA_ACCESS_HATCH_SB_MID
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 2 |  | True | LAZA_ACCESS_HATCH_PS_MID | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch PS Mid Nr.40 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.LAZA_ACCESS_HATCH_PS_MID
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 3 |  | True | LAZA_ACCESS_HATCH_SB_AFT | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch SB Aft Nr.41 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.LAZA_ACCESS_HATCH_SB_AFT
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 4 |  | True | LAZA_ACCESS_HATCH_PS_AFT | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Lazarette Access Hatch PS Aft Nr.42 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.LAZA_ACCESS_HATCH_PS_AFT
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 5 |  | True | AFT_DECKH_VENT_HATCH | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Aft Deckhouse Ventilation Hatch Nr.44 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.AFT_DECKH_VENT_HATCH
R2.4 |  | Bool | KEB1 | DI26 | 750-1415 | 6 |  | True | SBP_PS_CLOSED_LOCKED | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | PS Side Boarding Platform Crew Closed & Locked |  |  |  | 543W0002 | 4x3x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.SBP_PS_CLOSED_LOCKED
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 7 |  | True | VENT_SUPP_TECH_SPACE_REM_AVAIL | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Supply Technical Space Remote Available |  |  |  | 412.4W0010 | 2x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.VENT_SUPP_TECH_SPACE_REM_AVAIL
R2.2 |  | Bool | KEB1 | DI26 | 750-1415 | 8 |  | True | VENT_SUPP_TECH_SPACE_RUNNING | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Supply Technical Space Running | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_SUPP_TECH_SPACE_RUNNING
R2.2 |  | Bool | KEB1 | DI27 | 750-1415 | 1 |  | True | VENT_EXTR_TECH_SPACE_REM_AVAIL | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Extractor Technical Space Remote Available |  |  |  | 412.4W0009 | 2x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.VENT_EXTR_TECH_SPACE_REM_AVAIL
R2.2 |  | Bool | KEB1 | DI27 | 750-1415 | 2 |  | True | VENT_EXTR_TECH_SPACE_RUNNING | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Extractor Technical Space Running | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_EXTR_TECH_SPACE_RUNNING
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 3 |  | True | BATT_VENT_AFT_PS_ON_RUN | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS On / Run |  |  |  | 412.3W0023 | 4x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_PS_ON_RUN
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 4 |  | True | BATT_VENT_AFT_PS_ON_FAULT | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS Fault | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_PS_ON_FAULT | [12 empty] | 95 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 5 |  | True | BATT_VENT_AFT_PS_ON_READY | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS Ready | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_PS_ON_READY
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 6 |  | True | BATT_VENT_AFT_SB_ON_RUN | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB On / Run |  |  |  | 412.3W0024 | 4x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_SB_ON_RUN
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 7 |  | True | BATT_VENT_AFT_SB_ON_FAULT | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB Fault | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_SB_ON_FAULT | [12 empty] | 98 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 8 |  | True | BATT_VENT_AFT_SB_ON_READY | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB Ready | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_SB_ON_READY
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 1 |  | True | DRAIN_VLV_Y01_POS_OVERBOARD | +CB.1 |  | 1000 | 250000 TECHWATER | 25004014_1 | Drain water Valve Y01 Position Overboard |  |  |  | ????? | 2x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.DRAIN_VLV_Y01_POS_OVERBOARD
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 2 |  | True | DRAIN_VLV_Y01_POS_TO_PURO | +CB.1 |  | 1000 | 250000 TECHWATER | 25004014_1 | Drain water Valve Y01 Position to Puro | [6 empty] | Mqtt1 | 250000 TECHWATER | $.DRAIN_VLV_Y01_POS_TO_PURO
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 3 |  | True | TECH_WATER_CHLORINE_UNIT_ALARM | +CB.1 |  | 1000 | 250000 TECHWATER | 25004035 | Chlorine Dosing Unit Common Alarm |  |  |  | 421.2W0020 | 2x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WATER_CHLORINE_UNIT_ALARM | [12 empty] | 102 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 4 |  | True | MTS_INLET_FIRE_FLAP_RELEASED | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_1 | Main Technical Space Inlet Fire Flap Released |  |  |  | 415W0007 | 4x2x0.75 |  | Mqtt1 | 250000 TECHWATER | $.MTS_INLET_FIRE_FLAP_RELEASED | [12 empty] | 103 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 5 |  | True | MTS_INLET_FIRE_FLAP_FULLY_RESET | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_1 | Main Technical Space Inlet Fire Flap Fully Reset | [6 empty] | Mqtt1 | 250000 TECHWATER | $.MTS_INLET_FIRE_FLAP_FULLY_RESET | [12 empty] | 104 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 6 |  | True | MTS_EXHAUST_FIRE_FLAP_RELEASED | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_2 | Main Technical Space Exhaust Fire Flap Released |  |  |  | 415W0008 | 4x2x0.75 |  | Mqtt1 | 250000 TECHWATER | $.MTS_EXHAUST_FIRE_FLAP_RELEASED | [12 empty] | 105 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 7 |  | True | MTS_EXHAUST_FIRE_FLAP_FULLY_RESET | +CB.1 |  | 1000 | 250000 TECHWATER | 35005031_2 | Main Technical Space Exhaust Fire Flap Fully Reset | [6 empty] | Mqtt1 | 250000 TECHWATER | $.MTS_EXHAUST_FIRE_FLAP_FULLY_RESET | [12 empty] | 106 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI28 | 750-1415 | 8 |  | True | HELM_PS_OUT_DISP_ON_OFF | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS Out Display On/Off |  |  |  | 58A-C131 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_PS_OUT_DISP_ON_OFF
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 1 |  | True | HELM_PS_OUT_DISP_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS Out Display Toggle |  |  |  | IW0152 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_PS_OUT_DISP_TOGG
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 2 |  | True | HELM_PS_IN_DISP_ON_OFF | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Display On/Off |  |  |  | 58A-C131 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_PS_IN_DISP_ON_OFF
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 3 |  | True | HELM_PS_IN_DISP_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Display Toggle |  |  |  | 58A-C101 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_PS_IN_DISP_TOGG
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 4 |  | True | HELM_PS_IN_DISP_AMCS | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Display AMCS Direct |  |  |  | 58A-C101 |  |  | Mqtt1 | KVM SWITCHING | $.HELM_PS_IN_DISP_AMCS
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 5 |  | True | HELM_PS_MUTE_AMCS | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS Mute AMCS |  |  |  | IW0010 | SPEC |  | Mqtt1 | 450000 AMCS | $.HELM_PS_MUTE_AMCS
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 6 |  | True | HELM_PS_BACKLIGHT_UP_DOWN | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS Backlight Up/Down |  |  |  | 58A-C131 | CAT7 |  | Mqtt1 | 450000 AMCS | $.HELM_PS_BACKLIGHT_UP_DOWN
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 7 |  | True | HELM_PS_CREW_CALL | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS Crew Call |  |  |  | IW0010 | SPEC |  | Mqtt1 | 450000 AMCS | $.HELM_PS_CREW_CALL | [12 empty] | 114 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI29 | 750-1415 | 8 |  | True | SHIPS_OFF_DISP_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Ships Office Display Toggle |  |  |  | 58A-C49 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.SHIPS_OFF_DISP_TOGG
R2.2 |  | Bool | KEB1 | DI30 | 750-1415 | 1 |  | True | DB_GEN_SERVICE_14E1_01V01_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 01V01 Failure |  |  |  | 126W0003 | 7x2x0.75 |  | Mqtt1 | 450000 24VDC SYSTEM | $.DB_GEN_SERVICE_14E1_01V01_FAULT | [12 empty] | 116 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI30 | 750-1415 | 2 |  | True | DB_GEN_SERVICE_14E1_01V02_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 01V02 Failure | [6 empty] | Mqtt1 | 450000 24VDC SYSTEM | $.DB_GEN_SERVICE_14E1_01V02_FAULT | [12 empty] | 117 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 3 |  | True | DB_GEN_SERVICE_14E1_02V01_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 02V01 Failure | [6 empty] | Mqtt1 | 450000 24VDC SYSTEM | $.DB_GEN_SERVICE_14E1_02V01_FAULT | [12 empty] | 118 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 4 |  | True | DB_GEN_SERVICE_14E1_02V02_FAULT | +CB.1 |  | 1000 | 450000 24VDC SYSTEM |  | 24 Vdc DB General Service 14E1 02V02 Failure | [6 empty] | Mqtt1 | 450000 24VDC SYSTEM | $.DB_GEN_SERVICE_14E1_02V02_FAULT | [12 empty] | 119 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.3 |  | Bool | KEB1 | DI30 | 750-1415 | 5 |  | True | SEA_WATER_COOL_PMP1_RUNNING | +CB.1 |  | 1000 | 380000 SEAWATER |  | Sea Water Cooling Pump 1 Running |  |  |  | 373W0029 | 4x2x0,75 |  | Mqtt1 | 380000 SEAWATER | $.SEA_WATER_COOL_PMP1_RUNNING
R2.3 |  | Bool | KEB1 | DI30 | 750-1415 | 6 |  | True | SEA_WATER_COOL_PMP1_REMOTE | +CB.1 |  | 1000 | 380000 SEAWATER |  | Sea Water Cooling Pump 1 Remote Available | [6 empty] | Mqtt1 | 380000 SEAWATER | $.SEA_WATER_COOL_PMP1_REMOTE
R2.3 |  | Bool | KEB1 | DI30 | 750-1415 | 7 |  | True | Spare_DI30_7 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.3 |  | Bool | KEB1 | DI30 | 750-1415 | 8 |  | True | Spare_DI30_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 1 |  | True | PCS_CB.10_COM_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Common Alarm |  |  |  | =16.11-W232 | 7x2x0.75 |  | Mqtt1 | 150000 PCS | $.PCS_CB.10_COM_ALARM | [12 empty] | 124 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  | 1 |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 2 |  | True | PCS_CB.10_24VDC_SERV_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 24Vdc Service Failure | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_24VDC_SERV_FAIL | [12 empty] | 125 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 3 |  | True | PCS_CB.10_24VDC_EMERG_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 24Vdc Emergency Failure | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_24VDC_EMERG_FAIL | [12 empty] | 126 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 4 |  | True | PCS_CB.10_POWER_DISTR_INS | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Power Distribution Insulation | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_POWER_DISTR_INS | [12 empty] | 127 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 5 |  | True | PCS_CB.10_HYDR_PRESS_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Hydraulic Pressure Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_HYDR_PRESS_ALARM | [12 empty] | 128 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 6 |  | True | PCS_CB.10_OIL_LEV_ALARM_SEAL_TANK | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Oil level Alarm Shaft Seal Tank | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_OIL_LEV_ALARM_SEAL_TANK | [12 empty] | 129 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 7 |  | True | PCS_CB.10_GEAR_OIL_LEV_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Gear Oil Level Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_GEAR_OIL_LEV_ALARM | [12 empty] | 130 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI31 | 750-1415 | 8 |  | True | PCS_CB.10_GEAR_OIL_TEMP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Gear Oil Temperature Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_GEAR_OIL_TEMP_ALARM | [12 empty] | 131 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 1 |  | True | PCS_CB.10_OVERSP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Overspeed Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_OVERSP_ALARM | [12 empty] | 132 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 2 |  | True | PCS_CB.10_OVERL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Overload Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_OVERL_ALARM | [12 empty] | 133 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 3 |  | True | PCS_CB.10_AZI_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Azimuth Follow Up Failure/Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_AZI_FOLL_UP_FAIL_ALARM | [12 empty] | 134 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB1 | DI32 | 750-1415 | 4 |  | True | PCS_CB.10_PITCH_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.10 Thruster Pitch Follow Up Failure/Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.10_PITCH_FOLL_UP_FAIL_ALARM | [12 empty] | 135 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI32 | 750-1415 | 5 |  | True | DECK_SLIDE_WIND_DRIVE FAIL | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System Drive Failure |  |  |  | 601W005.3 | 19x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.DECK_SLIDE_WIND_DRIVE FAIL | [12 empty] | 136 |  |  |  |  | False |  | TS |  | Alaem | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI32 | 750-1415 | 6 |  | True | DECK_SLIDE_WIND_REM_AVAIL | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System Remote Available | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.DECK_SLIDE_WIND_REM_AVAIL
R2.4 |  | Bool | KEB1 | DI32 | 750-1415 | 7 |  | True | DECK_SLIDE_WIND_DRIVE_RUNN | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System Drive Running | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.DECK_SLIDE_WIND_DRIVE_RUNN
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 8 |  | True | Spare_DI32_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 1 |  | True | BILGE_FRAME68_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_1 | Water Sensor in Hull Fr.68 Alarm |  |  |  | 601W0001.2 | 7x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME68_ALARM | [12 empty] | 140 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 2 |  | True | BILGE_FRAME53_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_2 | Water Sensor in Hull Fr.53 Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME53_ALARM | [12 empty] | 141 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 3 |  | True | BILGE_BATT_COMP_5_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_10 | Water Sensor For Battery Compartment 5 | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_BATT_COMP_5_ALARM | [12 empty] | 142 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB1 | DI33 | 750-1415 | 4 |  | True | BILGE_BATT_COMP_6_ALARM | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001031_11 | Water Sensor For Battery Compartment 6 | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_BATT_COMP_6_ALARM | [12 empty] | 143 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 5 |  | True | W_TIGHT_HATCH_RM35_SEAL_INFLATED | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Seal Inflated |  |  |  | 535.1W0016 | 4x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM35_SEAL_INFLATED
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 6 |  | True | W_TIGHT_HATCH_RM35_DOOR_OPEN | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Door Open | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM35_DOOR_OPEN | [12 empty] | 145 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 7 |  | True | W_TIGHT_HATCH_RM35_POS_PROG_SWITCH | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Position Program Switch Exit Only Active | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM35_POS_PROG_SWITCH
R2.4 |  | Bool | KEB1 | DI33 | 750-1415 | 8 |  | True | W_TIGHT_HATCH_RM35_COMMON_ALARM | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-35 Common Alarm | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM35_COMMON_ALARM | [12 empty] | 147 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 1 |  | True | W_TIGHT_HATCH_RM36_SEAL_INFLATED | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Seal Inflated |  |  |  | 535.1W0002 | 4x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM36_SEAL_INFLATED
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 2 |  | True | W_TIGHT_HATCH_RM36_DOOR_OPEN | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Door Open | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM36_DOOR_OPEN | [12 empty] | 149 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 3 |  | True | W_TIGHT_HATCH_RM36_POS_PROG_SWITCH | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Position Program Switch Exit Only Active | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM36_POS_PROG_SWITCH
R2.4 |  | Bool | KEB1 | DI34 | 750-1415 | 4 |  | True | W_TIGHT_HATCH_RM36_COMMON_ALARM | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Hatch RM-36 Common Alarm | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_HATCH_RM36_COMMON_ALARM | [12 empty] | 151 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.6 |  | Bool | KEB1 | DI34 | 750-1415 | 5 |  | True | BURGLAR_ALARM_206U01 | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U01 |  |  |  | 601W0005.2 |  |  | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALARM_206U01
R2.6 |  | Bool | KEB1 | DI34 | 750-1415 | 6 |  | True | BURGLAR_ALARM_206U02 | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U02 | [6 empty] | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALARM_206U02
R2.6 |  | Bool | KEB1 | DI34 | 750-1415 | 7 |  | True | BURGLAR_ALARM_206U03 | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U03 |  |  |  | 206W0015 |  |  | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALARM_206U03
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 8 |  | True | Spare_DI34_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 1 |  | True | Spare_DI35_1 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 2 |  | True | Spare_DI35_2 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 3 |  | True | Spare_DI35_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 4 |  | True | Spare_DI35_4 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 5 |  | True | Spare_DI35_5 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 6 |  | True | Spare_DI35_6 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 7 |  | True | Spare_DI35_7 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 8 |  | True | Spare_DI35_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 1 |  | True | Spare_DI36_1 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 2 |  | True | Spare_DI36_2 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 3 |  | True | Spare_DI36_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 4 |  | True | Spare_DI36_4 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 5 |  | True | Spare_DI36_5 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 6 |  | True | Spare_DI36_6 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 7 |  | True | Spare_DI36_7 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 8 |  | True | Spare_DI36_8 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.2 |  | Float | KEB1 | AI20 | 750-455 | 1 |  | True | FLOW_LOWER_SALOON_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_30 | Flow Sensor Lower Saloon Cold Water |  |  |  | 601W0001 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_LOWER_SALOON_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB1 | AI20 | 750-455 | 2 |  | True | FLOW_DAYHEAD_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_31 | Flow Sensor Dayhead Cold Water |  |  |  | 601W0003 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_DAYHEAD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI20 | 750-455 | 3 |  | True | FLOW_GUEST_CABIN_SB_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_33 | Flow Sensor Guest Cabin SB Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_CABIN_SB_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI20 | 750-455 | 4 |  | True | FLOW_GUEST_CABIN_SB_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_32 | Flow Sensor Guest Cabin SB Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_CABIN_SB_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 1 |  | True | FLOW_GUEST_CABIN_PS_FWD_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_36 | Flow Sensor Guest Cabin PS Fwd Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_CABIN_PS_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 2 |  | True | FLOW_GUEST_CABIN_PS_FWD_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_34 | Flow Sensor Guest Cabin PS Fwd Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_CABIN_PS_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 3 |  | True | FLOW_GUEST_CABIN_PS_AFT_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_38 | Flow Sensor Guest Cabin PS Aft Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_CABIN_PS_AFT_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI21 | 750-455 | 4 |  | True | FLOW_GUEST_CABIN_PS_AFT_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_35 | Flow Sensor Guest Cabin PS Aft Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_CABIN_PS_AFT_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 1 |  | True | FLOW_MASTER_CABIN_SB_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_40 | Flow Sensor Master Cabin SB Hot Water |  |  |  | 601W0001 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_MASTER_CABIN_SB_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 2 |  | True | FLOW_MASTER_CABIN_SB_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_37 | Flow Sensor Master Cabin SB Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_MASTER_CABIN_SB_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 3 |  | True | FLOW_MASTER_CABIN_PS_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_42 | Flow Sensor Master Cabin PS Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_MASTER_CABIN_PS_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI22 | 750-455 | 4 |  | True | FLOW_MASTER_CABIN_PS_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_39 | Flow Sensor Master Cabin PS Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_MASTER_CABIN_PS_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 1 |  | True | FLOW_LAZARET_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_43 | Flow Sensor Lazaret Hot Water |  |  |  | 601W0025 | 10x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_LAZARET_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 2 |  | True | FLOW_LAZARET_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_41 | Flow Sensor Lazaret Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_LAZARET_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 3 |  | True | FLOW_WATER_SOFTNER_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001124 | Flow Sensor Water Softner Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_WATER_SOFTNER_COLD_WATER | [8 empty] | 0.1 | 75 | l/min
R2.2 |  | Float | KEB1 | AI23 | 750-455 | 4 |  | True | FLOW_MAIN_TECH_SPACE_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001123_1 | Flow Sensor Main Technical Space Hot Water |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_MAIN_TECH_SPACE_HOT_WATER | [8 empty] | 5 | 300 | l/min
R2.2 |  | Float | KEB1 | AI24 | 750-455 | 1 |  | True | FLOW_MAIN_TECH_SPACE_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001037_1 | Flow Sensor Main Technical Space Cold Water |  |  |  | 601W0004.2 | 7x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_MAIN_TECH_SPACE_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI24 | 750-455 | 2 |  | True | FLOW_MAIN_TECH_SPACE_FR45_COLD_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001123_2 | Flow Sensor Main Technical Space FR45 Bilge Area Cold Water |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_MAIN_TECH_SPACE_FR45_COLD_WATER | [8 empty] | 5 | 300 | l/min
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 3 |  | True | LEVEL_FRESH_WATER_TANK_1_FR_45_PS | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001019_1 | Level Sensor Fresh Water Tank 1 FR 45 PS |  |  |  | 421.1W0088 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.LEVEL_FRESH_WATER_TANK_1_FR_45_PS | [8 empty] | 4 | 20 | 4-20mA
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 4 |  | True | LEVEL_FRESH_WATER_TANK_2_FR_45_SB | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001019_2 | Level Sensor Fresh Water Tank 2 FR 45 SB |  |  |  | 421.1W0089 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.LEVEL_FRESH_WATER_TANK_2_FR_45_SB | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 1 |  | True | FLOW_DAYHEAD_HOT_WATER | +CB.1 |  | 1000 | 250000 FRESH WATER | 250010037_C2 | Flow Sensor Dayhead Hot Water |  |  |  | 601W0003 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_DAYHEAD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 2 |  | True | Spare_AI25_2 | +CB.1 |  | 1000 | SPARE |  | Spare | [17 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 3 |  | True | ACC_SENSOR_2_OUTPX | +CB.1 |  | 1000 | 450000 AMCS | 45019001_2 | Acceleration Sensor 2 Output X |  |  |  | 601W0005.2 | 14x2x0,75 |  | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_2_OUTPX | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI25 | 750-455 | 4 |  | True | ACC_SENSOR_2_OUTPY | +CB.1 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 2 Output Y | [6 empty] | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_2_OUTPY | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI26 | 750-455 | 1 |  | True | ACC_SENSOR_2_OUTPZ | +CB.1 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 2 Output Z | [6 empty] | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_2_OUTPZ | [8 empty] | 4 | 20 | 4-20mA
R1.8 |  | Float | KEB1 | AI26 | 750-455 | 2 |  | True | PNEUMATIC_PRESSURE | +CB.1 |  | 1000 | 290000 PNEUMATIC | 29001019 | Pressure |  |  |  | 425W0003 | 2x2x0,75 |  | Mqtt1 | 290000 PNEUMATIC | $.PNEUMATIC_PRESSURE | [8 empty] | 0 | 16 | Bar |  | 197 |  |  | 6 |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB1 | AI26 | 750-455 | 3 |  | True | LEVEL_GREY_WATER_TANK_AFT_SB | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_1 | Level Sensor Greywater Tank Aft FR 53 SB |  |  |  | 601W0001.2 | 7x2x0,75 |  | Mqtt1 | 340000 SEWAGE | $.LEVEL_GREY_WATER_TANK_AFT_SB | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI26 | 750-455 | 4 |  | True | LEVEL_BLACK_GREY_WATER_TANK_AFT_PS | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_2 | Level Sensor Black & Greywater Tank FR 48 PS |  |  |  | 601W0004.2 | 7x2x0,75 |  | Mqtt1 | 340000 SEWAGE | $.LEVEL_BLACK_GREY_WATER_TANK_AFT_PS | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI27 | 750-455 | 1 |  | True | LEVEL_SLUDGE_TANK_PS | +CB.1 |  | 1000 | 340000 SEWAGE | 34001025_3 | Level Sensor Sludge Tank FR 50 | [6 empty] | Mqtt1 | 340000 SEWAGE | $.LEVEL_SLUDGE_TANK_PS | [8 empty] | 4 | 20 | 4-20mA
R1.10 | Waiting on info | Float | KEB1 | AI27 | 750-455 | 2 |  | True | MAIN_DECKH_VENT_HATCH_SB_PERC | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch SB Nr.33 Percentage Open |  |  |  | 535W0020 | 4x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.MAIN_DECKH_VENT_HATCH_SB_PERC | [8 empty] | 0 | 100 | %
R1.10 | Waiting on info | Float | KEB1 | AI27 | 750-455 | 3 |  | True | MAIN_DECKH_VENT_HATCH_PS_PERC | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch PS Nr.34 Percentage Open |  |  |  | 535W0022 | 4x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.MAIN_DECKH_VENT_HATCH_PS_PERC | [8 empty] | 0 | 100 | %
R1.10 | Waiting on info | Float | KEB1 | AI27 | 750-455 | 4 |  | True | AFT_DECKH_VENT_HATCH_PERC | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Aft Deckhouse Ventilation Hatch Nr.44 Percentage Open |  |  |  | ????? |  |  | Mqtt1 | 090000 DOORS HATCHES | $.AFT_DECKH_VENT_HATCH_PERC | [8 empty] | 0 | 100 | %
R1.10 | Waiting on info | Float | KEB1 | AI28 | 750-455 | 1 |  | True | TECH_WAT_SALINITY | +CB.1 |  | 1000 | 250000 TECHWATER |  | Salinity Sensor |  |  |  | ????? |  |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_SALINITY | [8 empty] | 4 | 20 | 4-20mA
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 2 |  | True | TECH_WAT_TANK1_LEVEL | +CB.1 |  | 1000 | 250000 TECHWATER | 25004025_1 | Level Sensor Technical Water Tank1 FR tbd SB |  |  |  | 421.2W0030 | 2x2x0.75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_TANK1_LEVEL | [8 empty] | 0 | 100 | % |  | 205 | 90 | 80 |  |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 3 |  | True | TECH_WAT_TANK2_LEVEL | +CB.1 |  | 1000 | 250000 TECHWATER | 25001025_2 | Level Sensor Technical Water Tank2 FR45 SB |  |  |  | 421.2W0031 | 2x2x0.75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_TANK2_LEVEL | [8 empty] | 0 | 100 | % |  | 206 | 90 | 80 |  |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB1 | AI28 | 750-455 | 4 |  | True | TECH_WAT_FLOW_CHARCOAL_FILTER_B01 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004037_4 | Flow Sensor Charcoal Filter B01 |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_CHARCOAL_FILTER_B01 | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI29 | 750-455 | 1 |  | True | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B04 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004037_3 | Flow Sensor Reel For Deckwash B04 |  |  |  | 601W0025 | 10x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_REEL_FOR_DECKWASH_B04 | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI29 | 750-455 | 2 |  | True | TECH_WAT_FLOW_CHARCOAL_FILTER_B02 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004038 | Flow Sensor Charcoal Filter B02 |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_CHARCOAL_FILTER_B02 | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI29 | 750-455 | 3 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B03 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004034_1 | Flow Sensor Adiabatic Cooling Line B03 | [6 empty] | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_ADIABATIC_COOL_B03 | [8 empty] | 4 | 20 | 4-20mA
R2.5 |  | Float | KEB1 | AI29 | 750-455 | 4 |  | True | FLOW_TECHNICAL_ROOM_ENERG_REC | +CB.1 |  |  | 250000 FRESH WATER | 25001139 | Flow Sensor Technocal Room Energy Recovery |  |  |  | 421.1W0174 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_TECHNICAL_ROOM_ENERG_REC | [8 empty] | 0.1 | 75 | l/min
R2.2 |  | Float | KEB1 | AI30 | 750-455 | 1 |  | True | Spare_AI30_1 | +CB.1 |  |  | SPARE |  | Spare Yard _True_+CB.1 | [17 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB1 | AI30 | 750-455 | 2 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B09 | +CB.1 |  | 1000 | 250000 TECHWATER | 25004034_4 | Flow Sensor Adiabatic Cooling Line B09 |  |  |  | 601W0004 | 19x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_ADIABATIC_COOL_B09 | [8 empty] | 4 | 20 | 4-20mA
R2.0 |  | Float | KEB1 | AI30 | 750-455 | 3 |  | True | Spare_AI30_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1 | [17 empty] | 4 | 20 | 4-20mA
R2.0 |  | Float | KEB1 | AI30 | 750-455 | 4 |  | True | Spare_AI30_4 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1 | [17 empty] | 4 | 20 | 4-20mA
R1.8 |  | Float | KEB1 | AI31 | 750-450 | 1 |  | True | STERN_THRUST_BEARING_TEMP_DE | +CB.1 |  | 1000 | 150000 PROPULSION |  | Stern Thrust Motor Bearing Temperature DE |  |  |  | =13.11-W130 | 8x2x0,75 |  | Mqtt1 | 150000 PROPULSION | $.STERN_THRUST_BEARING_TEMP_DE | [8 empty] | 0 | 150 | °C |  | 216 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.9 |  | Float | KEB1 | AI31 | 750-450 | 2 |  | True | STERN_THRUST_BEARING_TEMP_NDE | +CB.1 |  | 1000 | 150000 PROPULSION |  | Stern Thrust Motor Bearing Temperature NDE |  |  |  | =13.11-W131 | 8x2x0,75 |  | Mqtt1 | 150000 PROPULSION | $.STERN_THRUST_BEARING_TEMP_NDE | [8 empty] | 0 | 150 | °C |  | 217 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.9 |  | Float | KEB1 | AI31 | 750-450 | 3 |  | True | Spare_AI31_3 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1 | [17 empty] | 4 | 20 | °C
R2.5 |  | Float | KEB1 | AI31 | 750-450 | 4 |  | True | TEMP7_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_1 | Temperature Sensor S07 For Energy Recovery System |  |  |  | 421.1W0165 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.TEMP7_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.2 |  | Float | KEB1 | AI32 | 750-450 | 1 |  | True | TEMP4_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_4 | Temperature Sensor S04 For Energy Recovery System |  |  |  | 421.1W0090 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.TEMP4_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.2 |  | Float | KEB1 | AI32 | 750-450 | 2 |  | True | TEMP5_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_5 | Temperature Sensor S05 For Energy Recovery System | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.TEMP5_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.5 |  | Float | KEB1 | AI32 | 750-450 | 3 |  | True | TEMP8_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_3 | Temperature Sensor S08 For Energy Recovery System |  |  |  | 421.1W0164 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.TEMP8_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R2.5 |  | Float | KEB1 | AI32 | 750-450 | 4 |  | True | TEMP6_FOR_ENERGY_REC_SYSTEM | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001038_2 | Temperature Sensor S06 For Energy Recovery System |  |  |  | 421.1W0159.1 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.TEMP6_FOR_ENERGY_REC_SYSTEM | [8 empty] | -40 | 150 | °C
R1.8 |  | Bool | KEB1 | F2 | 750-610 | 1 |  | True | AmcsPlcPowerModule2FuseBlown | +CB.1 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 2 Fuse Blown | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule2FuseBlown | [12 empty] | 224 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | F2 | 750-610 | 2 |  | True | AmcsPlcPowerModule2PowerFailure | +CB.1 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB1 Power Module 2 Power Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule2PowerFailure | [12 empty] | 225 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB1 | AO60 | 750-555 | 1 |  | True | BATT_VENT_AFT_PS_SPEED | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT PS Speed |  |  |  | 412.3W0003 | 2x2x0,75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_PS_SPEED | [8 empty] | 0 | 100 | %
R2.0 |  | Float | KEB1 | AO60 | 750-555 | 2 |  | True | BATT_VENT_AFT_SB_SPEED | +CB.1 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation AFT SB Speed |  |  |  | 412.3W0006 | 2x2x0,75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_SB_SPEED | [8 empty] | 0 | 100 | %
R2.2 |  | Float | KEB1 | AO60 | 750-555 | 3 |  | True | SEW_TREAT_LEVEL_HOLDING_TANK | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant Level Holding Tank (DO???) |  |  |  | 447W0025 | 4x2x0,75 |  | Mqtt1 | 340000 SEWAGE | $.SEW_TREAT_LEVEL_HOLDING_TANK | [10 empty] | na
R2.2 |  | Float | KEB1 | AO60 | 750-555 | 4 |  | True | SEW_TREAT_LEVEL_SLUDGE_TANK | +CB.1 |  | 1000 | 340000 SEWAGE |  | Sewage Treatment Plant Level Sludge Tank (DO????) | [6 empty] | Mqtt1 | 340000 SEWAGE | $.SEW_TREAT_LEVEL_SLUDGE_TANK | [10 empty] | na
R2.3 |  | Bool | KEB1 | DO60 | 750-1500 | 1 |  | True | VENT_EXTR_TECH_SPACE_START_STOP | +CB.1 |  | 1000 | 350000 VENTILATION |  | Ventilation Extractor Technical Space Start Stop |  |  |  | ???? |  |  | Mqtt1 | 350000 VENTILATION | $.VENT_EXTR_TECH_SPACE_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 2 |  | True | STRIP_PUMP_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001004 | Stripping Pump Start/Stop |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 | 210000 BILGE FIFI | $.STRIP_PUMP_START_STOP
R2.3 |  | Bool | KEB1 | DO60 | 750-1500 | 3 |  | True | SEA_WATER_COOL_PMP1_START_STOP | +CB.1 |  | 1000 | 380000 SEAWATER |  | Sea Water Cooling Pump 1 Start/Stop |  |  |  | 373W0029 | 4x2x0,75 |  | Mqtt1 | 380000 SEAWATER | $.SEA_WATER_COOL_PMP1_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 4 |  | True | CHAIN_LOCK_PUMP_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001005 | Chain Locker Pump Start/Stop |  |  |  | 381W0010 | 19x1,5 |  | Mqtt1 | 210000 BILGE FIFI | $.CHAIN_LOCK_PUMP_START_STOP
R2.3 |  | Bool | KEB1 | DO60 | 750-1500 | 5 |  | True | GEN_SERV_PUMP1_FAULT_FDBCK | +CB.1 |  | 1000 | 210000 BILGE FIFI | [8 empty] | Mqtt1 | 210000 BILGE FIFI | $.GEN_SERV_PUMP1_FAULT_FDBCK
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 6 |  | True | SUBMERS_PUMP1_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_1 | Submersible Pump 1 Start/Stop |  |  |  | 381W0009 | 7x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP1_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 7 |  | True | SUBMERS_PUMP2_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_2 | Submersible Pump 2 Start/Stop |  |  |  | 381W0085 | 4x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP2_START_STOP
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 8 |  | True | SUBMERS_PUMP3_START_STOP | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001006_3 | Submersible Pump 3 Start/Stop |  |  |  | 381W0009 | 7x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.SUBMERS_PUMP3_START_STOP
R1.0 | Not in Alewijnse drawings | Bool | KEB1 | DO60 | 750-1500 | 9 |  | True | SEPARATOR_START | +CB.1 |  | 1000 | 210000 BILGE FIFI | 21001007 | Bilge Separator Start |  |  |  | ????? |  |  | Mqtt1 | 210000 BILGE FIFI | $.SEPARATOR_START
R2.2 |  | Bool | KEB1 | DO60 | 750-1500 | 10 |  | True | ZEROING_ACC_SENSOR_1 | +CB.1 |  | 1000 | 450000 AMCS |  | Zeroing acc Sensor 1 |  |  |  | 601W0005,2 | 14x2x20,75 |  | Mqtt1 | 450000 AMCS | $.ZEROING_ACC_SENSOR_1
R2.4 |  | Bool | KEB1 | DO60 | 750-1500 | 11 |  | True | DECK_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Deckhouse Sliding Window System On/Off |  |  |  | 601W0005.3 | 19x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.DECK_SLIDE_WIND_ON_OFF
R1.3 |  | Bool | KEB1 | DO60 | 750-1500 | 12 |  | True | ACTIVATE_HULL_TEMP_MEASUREMENT | +CB.1 |  | 1000 | 450000 AMCS |  | Activate Hull Temperature measurement |  |  |  | INTERNAL |  |  | Mqtt1 | 450000 AMCS | $.ACTIVATE_HULL_TEMP_MEASUREMENT
R1.5 |  | Bool | KEB1 | DO60 | 750-1500 | 13 |  | True | TRANS_PUMP_BLCK_WAT_START_STOP | +CB.1 |  | 1000 | 340000 SEWAGE | 34001001 | Transfer Pump 2 Blackwater Start/Stop |  |  |  | 447W0003 | 10x1,5 |  | Mqtt1 | 340000 SEWAGE | $.TRANS_PUMP_BLCK_WAT_START_STOP
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 14 |  | True | TRANS_PUMP_GREY_WAT_START_STOP | +CB.1 |  | 1000 | 340000 SEWAGE | 34001002 | Transfer Pump 1 Greywater Start/Stop |  |  |  | 447W0007 | 7x1,5 |  | Mqtt1 | 340000 SEWAGE | $.TRANS_PUMP_GREY_WAT_START_STOP
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 15 |  | True | PUMP_FWD_GREY_WAT_START_STOP | +CB.1 |  | 1000 | 340000 SEWAGE | 34001003 | Pump 3 Fwd Greywater Start/Stop |  |  |  | 447W0003 | 10x1,5 |  | Mqtt1 | 340000 SEWAGE | $.PUMP_FWD_GREY_WAT_START_STOP
R2.5 |  | Bool | KEB1 | DO60 | 750-1500 | 16 |  | True | FRESH_WATER_CIRC_PUMP_ON_OFF | +CB.1 |  | 1000 | 250000 FRESH WATER | 25001150 | Fresh Water Circulation Pump On/Off |  |  |  | 421.1W0172 | 2x2x0.75 |  | Mqtt1 | 250000 FRESH WATER | $.FRESH_WATER_CIRC_PUMP_ON_OFF
R2.6 |  | Bool | KEB1 | DO61 | 750-1500 | 1 |  | True | BURGLAR_ALRM_SYSTEM_ON_OFF | +CB.1 |  | 1000 | 450000 BURGLAR |  | Burglar System On/Off |  |  |  | 206W0031 |  |  | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALRM_SYSTEM_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 2 |  | True | VENT_FP_FR10_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_1 | Ventilation Forepeak FR10 PS On/Off |  |  |  | 412.5W0003 | 10x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.VENT_FP_FR10_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 3 |  | True | VENT_FP_FR10_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_1 | Ventilation Forepeak FR10 PS Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_FP_FR10_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 4 |  | True | VENT_LOCK_FR19_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_2 | Ventilation Locker FR19 PS On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR19_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 5 |  | True | VENT_LOCK_FR19_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_2 | Ventilation Locker FR19 PS Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR19_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 6 |  | True | VENT_LOCK_FR27_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_3 | Ventilation Locker FR27 PS On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR27_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 7 |  | True | VENT_LOCK_FR27_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_3 | Ventilation Locker FR27 PS Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR27_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 8 |  | True | VENT_LOCK_FR27_SB_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_4 | Ventilation Locker FR27 SB On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR27_SB_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 9 |  | True | VENT_LOCK_FR27_SB_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_4 | Ventilation Locker FR27 SB Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR27_SB_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 10 |  | True | VENT_LOCK_FR40_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_5 | Ventilation Locker FR40 PS On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR40_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 11 |  | True | VENT_LOCK_FR40_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_5 | Ventilation Locker FR40 PS Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR40_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 12 |  | True | VENT_LOCK_FR40_SB_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_6 | Ventilation Locker FR40 SB On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR40_SB_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 13 |  | True | VENT_LOCK_FR40_SB_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_6 | Ventilation Locker FR40 SB Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR40_SB_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 14 |  | True | VENT_LOCK_FR48_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_7 | Ventilation Locker FR48 PS On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR48_PS_ON_OFF
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 15 |  | True | VENT_LOCK_FR48_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_7 | Ventilation Locker FR48 PS Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LOCK_FR48_PS_SPEED_LOW_HIGH
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 16 |  | True | VENT_LAZ_FR73_PS_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_8 | Ventilation Lazarette FR73 PS On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LAZ_FR73_PS_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 1 |  | True | VENT_LAZ_FR73_PS_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_8 | Ventilation Lazarette FR73 PS Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LAZ_FR73_PS_SPEED_LOW_HIGH
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 2 |  | True | VENT_LAZ_FR73_SB_ON_OFF | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_9 | Ventilation Lazarette FR73 SB On/Off | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LAZ_FR73_SB_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 3 |  | True | VENT_LAZ_FR73_SB_SPEED_LOW_HIGH | +CB.1 |  | 1000 | 350000 VENTILATION | 35002266_9 | Ventilation Lazarette FR73 SB Speed Low/High | [6 empty] | Mqtt1 | 350000 VENTILATION | $.VENT_LAZ_FR73_SB_SPEED_LOW_HIGH
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 4 |  | True | TECH_WAT_VALVE_COLD_AIR_FR68_Y03_OPEN_CLOSE | +CB.1 |  | 1000 | 250000 TECHWATER | 25004020_1 | Valve For Cold Air Cooling Water FR68 Y03 |  |  |  | 421.2W0021 | 2x2,5 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_VALVE_COLD_AIR_FR68_Y03_OPEN_CLOSE
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 5 |  | True | TECH_WAT_VALVE_COLD_AIR_FR32_Y04_OPEN_CLOSE | +CB.1 |  | 1000 | 250000 TECHWATER | 25004020_2 | Valve For Cold Air Cooling Water FR32 Y04 |  |  |  | 421.2W0022 | 2x2,5 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_VALVE_COLD_AIR_FR32_Y04_OPEN_CLOSE
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 6 |  | True | TECH_WAT_VALVE_COLD_AIR_FR32_Y05_OPEN_CLOSE | +CB.1 |  | 1000 | 250000 TECHWATER | 25004020_3 | Valve For Cold Air Cooling Water FR32 Y05 |  |  |  | 421.2W0023 | 2x2,5 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_VALVE_COLD_AIR_FR32_Y05_OPEN_CLOSE
R2.1 |  | Bool | KEB1 | DO62 | 750-1500 | 7 |  | True | HELM_PS_IN_MOUSE_TOGG | +CB.1 |  | 1000 | KVM SWITCHING |  | Helmstation PS In Mouse Toggle |  |  |  | 25A-C136 | 2x2x0.5 |  | Mqtt1 | KVM SWITCHING | $.HELM_PS_IN_MOUSE_TOGG
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 8 |  | True | HELM_PS_AMCS_MUTE_FB | +CB.1 |  | 1000 | 450000 AMCS |  | Helmstation PS AMCS Mute Feedback |  |  |  | =70.11-W279 | 7x2x0,75 |  | Mqtt1 | 450000 AMCS | $.HELM_PS_AMCS_MUTE_FB
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 9 |  | True | GEN_SERVICE_PUMP2_FLD_AVAIL_FDBCK | +CB.1 |  | 1000 | 210000 GENERAL SERVICE |  | General Service Pump 2 Field Available Feedback |  |  |  | 381W0003 | 7x1,5 |  | Mqtt1 | 210000 GENERAL SERVICE | $.GEN_SERVICE_PUMP2_FLD_AVAIL_FDBCK
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 10 |  | True | GEN_SERVICE_PUMP2_FLD_RUN_FDBCK | +CB.1 |  | 1000 | 210000 GENERAL SERVICE |  | General Service Pump 2 Field Running Feedback |  |  |  | 381W0003 |  |  | Mqtt1 | 210000 GENERAL SERVICE | $.GEN_SERVICE_PUMP2_FLD_RUN_FDBCK
R2.2 |  | Bool | KEB1 | DO62 | 750-1500 | 11 |  | True | GEN_SERVICE_PUMP2_FLD_FAULT_FDBCK | +CB.1 |  | 1000 | 210000 GENERAL SERVICE |  | General Service Pump 2 Field Fault Feedback |  |  |  | 381W0003 |  |  | Mqtt1 | 210000 GENERAL SERVICE | $.GEN_SERVICE_PUMP2_FLD_FAULT_FDBCK
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 12 |  | True | AFT_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Cockpit AFT Sliding Window1~4 System On/Off |  |  |  | 827.1W0004 | 1x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.AFT_SLIDE_WIND_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 13 |  | True | PS_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Cockpit PS Sliding Window5~6 System On/Off |  |  |  | 827.1W0005 | 1x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.PS_SLIDE_WIND_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 14 |  | True | SB_SLIDE_WIND_ON_OFF | +CB.1 |  | 1000 | 090000 DOORS HATCHES |  | Owners Cockpit SB Sliding Window7~8 System On/Off |  |  |  | 827.1W0006 | 1x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.SB_SLIDE_WIND_ON_OFF
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 15 |  | True | Spare_DO62_15 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
R2.0 |  | Bool | KEB1 | DO62 | 750-1500 | 16 |  | True | Spare_DO62_16 | +CB.1 |  | 1000 | SPARE |  | Spare Yard _True_+CB.1
| True | [13 empty] | Serial Interface - KEC1 Port1
| True | [13 empty] | Serial Interface - KEC1 Port2
| True | [13 empty] | Serial Interface - KEC1 Port3
| True | [13 empty] | Serial Interface - KEC1 Port4
| True | [13 empty] | ALARM CABINET - AMCS Crew Mess +CB.2
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 0 |  | True | GFDEnabled | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Ground Fault Diagnostics Enabled | [6 empty] | Mqtt1 | 450000 AMCS | $.GFDEnabled
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 2 |  | True | FieldVoltageAvailable | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Voltage Available | [6 empty] | Mqtt1 | 450000 AMCS | $.FieldVoltageAvailable
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 4 |  | True | PA24V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Pre-Alarm 24V | [6 empty] | Mqtt1 | 450000 AMCS | $.PA24V | [12 empty] | 285 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 5 |  | True | MA24V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Main-Alarm 24V | [6 empty] | Mqtt1 | 450000 AMCS | $.MA24V | [12 empty] | 286 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 6 |  | True | PA0V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Pre-Alarm 0V | [6 empty] | Mqtt1 | 450000 AMCS | $.PA0V | [12 empty] | 287 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | R1 | 750-626/020-002 | 7 |  | True | MA0V | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Distribution Insulation Main-Alarm 0V | [6 empty] | Mqtt1 | 450000 AMCS | $.MA0V | [12 empty] | 288 |  |  |  |  | True |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI00 | 750-1415 | 1 |  | True | AmcsPowerSupplyFailure | +CB.2 |  | 1000 | 450000 AMCS |  | CREW MESS AMCS KEB2 Power Supply Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPowerSupplyFailure | [12 empty] | 289 |  |  |  |  | False |  | TS |  | Alarm | Check Primary (G2) supply, Secundary (G3) supply and redundancy module (G1) |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI00 | 750-1415 | 2 |  | True | Spare_DI00_2 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.9 |  | Bool | KEB2 | DI00 | 750-1415 | 3 |  | True | Spare_DI00_3 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.9 |  | Bool | KEB2 | DI00 | 750-1415 | 4 |  | True | Spare_DI00_4 | +CB.2 |  | 1000 | SPARE |  | Spare
R0.4 |  | Bool | KEB2 | DI00 | 750-1415 | 5 |  | True | BridgeBuzzersPowerSupplyFailure | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Buzzers Power Supply Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.BridgeBuzzersPowerSupplyFailure | [12 empty] | 293 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R0.4 |  | Bool | KEB2 | DI00 | 750-1415 | 6 |  | True | BridgeAlarmPanelSilenceButton | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Alarm Panel Silence Button | [6 empty] | Mqtt1 | 450000 AMCS | $.BridgeAlarmPanelSilenceButton
R1.4 |  | Bool | KEB2 | DI00 | 750-1415 | 7 |  | True | OperatorBuzzersPowerSupplyFailure | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Buzzers Power Supply Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.OperatorBuzzersPowerSupplyFailure | [12 empty] | 295 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.4 |  | Bool | KEB2 | DI00 | 750-1415 | 8 |  | True | OperatorAlarmPanelSilenceButton | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Alarm Panel Silence Button | [6 empty] | Mqtt1 | 450000 AMCS | $.OperatorAlarmPanelSilenceButton
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 1 |  | True | UmsCabin1Silence | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Silence | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsCabin1Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 2 |  | True | UmsCabin2Silence | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Silence | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsCabin2Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 3 |  | True | UmsCabin3Silence | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Silence | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsCabin3Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 4 |  | True | Spare_DI01_4 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 5 |  | True | Spare_DI01_5 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 6 |  | True | Spare_DI01_6 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 7 |  | True | Spare_DI01_7 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 8 |  | True | Spare_DI01_8 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 1 |  | True | UmsCabin1Buzzer | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Buzzer | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsCabin1Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 2 |  | True | UmsCabin2Buzzer | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Buzzer | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsCabin2Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 3 |  | True | UmsCabin3Buzzer | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Buzzer | [6 empty] | Mqtt1 | 450000 AMCS | $.UmsCabin3Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 4 |  | True | BridgeAlarmPanelSilenceLight | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Alarm Panel Silence Light | [6 empty] | Mqtt1 | 450000 AMCS | $.BridgeAlarmPanelSilenceLight
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 5 |  | True | OperatorAlarmPanelSilenceLight | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Alarm Panel Silence Light | [6 empty] | Mqtt1 | 450000 AMCS | $.OperatorAlarmPanelSilenceLight
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 6 |  | True | MachinerySpaceBuzzerHorn | +CB.2 |  | 1000 | 450000 AMCS |  | Machinery Space Buzzer Horn | [6 empty] | Mqtt1 | 450000 AMCS | $.MachinerySpaceBuzzerHorn
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 7 |  | True | BridgeAlarmPanelBuzzer | +CB.2 |  | 1000 | 450000 AMCS |  | Bridge Alarm Panel Buzzer | [6 empty] | Mqtt1 | 450000 AMCS | $.BridgeAlarmPanelBuzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 8 |  | True | OperatorAlarmPanelBuzzer | +CB.2 |  | 1000 | 450000 AMCS |  | Operator Alarm Panel Buzzer | [6 empty] | Mqtt1 | 450000 AMCS | $.OperatorAlarmPanelBuzzer
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 1 |  | True | UMSCabin1Duty | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Duty | [6 empty] | Mqtt1 | 450000 AMCS | $.UMSCabin1Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 2 |  | True | UMSCabin1AlarmLed | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 1 Alarm Led | [6 empty] | Mqtt1 | 450000 AMCS | $.UMSCabin1AlarmLed
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 3 |  | True | UMSCabin2Duty | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Duty | [6 empty] | Mqtt1 | 450000 AMCS | $.UMSCabin2Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 4 |  | True | UMSCabin2AlarmLed | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 2 Alarm Led | [6 empty] | Mqtt1 | 450000 AMCS | $.UMSCabin2AlarmLed
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 5 |  | True | UMSCabin3Duty | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Duty | [6 empty] | Mqtt1 | 450000 AMCS | $.UMSCabin3Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 6 |  | True | UMSCabin3AlarmLed | +CB.2 |  | 1000 | 450000 AMCS |  | UMS Cabin 3 Alarm Led | [6 empty] | Mqtt1 | 450000 AMCS | $.UMSCabin3AlarmLed
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 7 |  | True | Spare_DO01_7 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 8 |  | True | Spare_DO01_8 | +CB.2 |  | 1000 | SPARE |  | Spare
R1.14_FAT |  | Bool | KEB2 | F1 | 750-610 | 1 |  | True | AmcsPlcPowerModule1InternalFuseBlown | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 1 Internal Fuse Blown | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule1InternalFuseBlown | [12 empty] | 321 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.14_FAT |  | Bool | KEB2 | F1 | 750-610 | 2 |  | True | AmcsPlcPowerModule1PowerFailure | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 1 Power Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule1PowerFailure | [12 empty] | 322 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 1 |  | True | SEA_WATER_COOL_PMP2_RUNNING | +CB.2 |  | 1000 | 380000 SEAWATER |  | Sea Water Cooling Pump 2 Running |  |  |  | 373W0028 | 4x2x0,75 |  | Mqtt1 | 380000 SEAWATER | $.SEA_WATER_COOL_PMP2_RUNNING
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 2 |  | True | SEA_WATER_COOL_PMP2_REMOTE | +CB.2 |  | 1000 | 380000 SEAWATER |  | Sea Water Cooling Pump 2 Remote Available | [6 empty] | Mqtt1 | 380000 SEAWATER | $.SEA_WATER_COOL_PMP2_REMOTE
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 3 |  | True | BILGE_FRAME48_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_3 | Water Sensor in Hull Fr.48 Alarm |  |  |  | 601W0020 | 19x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME48_ALARM | [12 empty] | 325 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 4 |  | True | BILGE_FRAME46_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_4 | Water Sensor in Hull Fr.46 Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME46_ALARM | [12 empty] | 326 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 5 |  | True | BILGE_FRAME38_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_5 | Water Sensor in Hull Fr.38 Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME38_ALARM | [12 empty] | 327 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 6 |  | True | BILGE_FRAME30_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_6 | Water Sensor in Hull Fr.30 Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME30_ALARM | [12 empty] | 328 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 7 |  | True | BILGE_FRAME15_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_7 | Water Sensor in Hull Fr.15 Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME15_ALARM | [12 empty] | 329 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI20 | 750-1415 | 8 |  | True | BILGE_FRAME13_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_8 | Water Sensor in Hull Fr.13 Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME13_ALARM | [12 empty] | 330 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 1 |  | True | BILGE_FRAME47SB_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_9 | Water Sensor in Hull Fr.47 SB Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME47SB_ALARM | [12 empty] | 331 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB2 | DI21 | 750-1415 | 2 |  | True | FIRE_SLIDE_DOOR_GALL_CREW | +CB.2 |  |  | 090000 DOORS HATCHES |  | Fire Sliding Door Galley Crew Mess |  |  |  | 533W002 | 2x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.FIRE_SLIDE_DOOR_GALL_CREW
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 3 |  | True | Spare_DI21_3 | +CB.2 |  |  | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 4 |  | True | BILGE_FRAME38PS_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_12 | Water Sensor in Hull Fr.38 PS Alarm |  |  |  | 601W0020 | 19x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME38PS_ALARM | [12 empty] | 334 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 5 |  | True | BILGE_FRAME38SB_ALARM | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001031_13 | Water Sensor in Hull Fr.38 SB Alarm | [6 empty] | Mqtt1 | 210000 BILGE FIFI | $.BILGE_FRAME38SB_ALARM | [12 empty] | 335 |  |  |  |  | False | 10 | TS | BRG | Emergency | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 6 |  | True | BCKUP_GEN_SERV_PUMP_REM_AVAIL | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001003 | Backup General Service Pump Remote Available |  |  |  | 381W0008 | 2x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.BCKUP_GEN_SERV_PUMP_REM_AVAIL
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 7 |  | True | Spare_DI21_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI21 | 750-1415 | 8 |  | True | Spare_DI21_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 1 |  | True | CAPT_CAB_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Captains Cabin Display Toggle |  |  |  | 58A-C60 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.CAPT_CAB_DISP_TOGG
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 2 |  | True | MISSION_RM_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Mission Room Display Toggle |  |  |  | 58A-C26 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.MISSION_RM_DISP_TOGG
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 3 |  | True | CREW_MESS_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Crew Mess Display Toggle |  |  |  | 58A-C160 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.CREW_MESS_DISP_TOGG
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 4 |  | True | Spare_DI22_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DI22 | 750-1415 | 5 |  | True | Spare_DI22_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI22 | 750-1415 | 6 |  | True | DECK_CRANE_GEN_ALARM | +CB.2 |  | 1000 | 750000 DECK EQUIP | 22AJB7/10.0 | General Alarm |  |  |  | 601W0022 | 19x2x0,75 |  | Mqtt1 | 750000 DECK EQUIP | $.DECK_CRANE_GEN_ALARM | [12 empty] | 344 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI22 | 750-1415 | 7 |  | True | MOB_TENDER_HATCH_CL_LOCK | +CB.2 |  | 1000 | 750000 DECK EQUIP | 22AJB7/10.1 | MOB Tender Hatch Closed & Locked | [6 empty] | Mqtt1 | 750000 DECK EQUIP | $.MOB_TENDER_HATCH_CL_LOCK
R2.2 |  | Bool | KEB2 | DI22 | 750-1415 | 8 |  | True | GUEST_TENDER_HATCH_CL_LOCK | +CB.2 |  | 1000 | 750000 DECK EQUIP | 22AJB7/10.2 | Guest Tender Hatch Closed & Locked | [6 empty] | Mqtt1 | 750000 DECK EQUIP | $.GUEST_TENDER_HATCH_CL_LOCK
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 1 |  | True | SAIL_STOR_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Sail Storage Hatch Nr.2 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.SAIL_STOR_HATCH
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 2 |  | True | FOREPEAK_ACC_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Forepeak Access Hatch Nr.3 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.FOREPEAK_ACC_HATCH
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 3 |  | True | DINGHY_STOR_ACC_FWD | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Dinghy Storage Access Fwd Nr.7A | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.DINGHY_STOR_ACC_FWD
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 4 |  | True | CRANE__HATCH_AFT | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Crane Hatch Aft Nr.7D | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.CRANE__HATCH_AFT
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 5 |  | True | FORESHIP_STOR_AREA_ACC_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Foreship Storage Area Access Hatch Nr.9 | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.FORESHIP_STOR_AREA_ACC_HATCH
R2.2 |  | Bool | KEB2 | DI23 | 750-1415 | 6 |  | True | CREW_ESCAPE_HATCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Crew Escape Hatch Nr.15 |  |  |  | 601W0029 | 19x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.CREW_ESCAPE_HATCH
R2.4 |  | Bool | KEB2 | DI23 | 750-1415 | 7 |  | True | Spare_DI23_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 8 |  | True | FIRE_DETECT_FAULT | +CB.2 |  | 1000 | 450000 FIREDETECTION |  | System Fault |  |  |  | 201W0502 | 4x2x0.75 |  | Mqtt1 | 450000 FIREDETECTION | $.FIRE_DETECT_FAULT | [12 empty] | 354 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.3 |  | Bool | KEB2 | DI24 | 750-1415 | 1 |  | True | Spare_DI24_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 2 |  | True | BATT_VENT_FWD_PS_ON_RUN | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS On / Run |  |  |  | 412.3W0010 | 7x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_PS_ON_RUN
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 3 |  | True | BATT_VENT_FWD_PS_ON_FAULT | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS Fault | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_PS_ON_FAULT | [12 empty] | 357 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 4 |  | True | BATT_VENT_FWD_PS_ON_READY | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS Ready | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_PS_ON_READY
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 5 |  | True | BATT_VENT_FWD_SB_ON_RUN | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB On / Run |  |  |  | 412.3W0011 | 7x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_SB_ON_RUN
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 6 |  | True | BATT_VENT_FWD_SB_ON_FAULT | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB Fault | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_SB_ON_FAULT | [12 empty] | 360 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI24 | 750-1415 | 7 |  | True | BATT_VENT_FWD_SB_ON_READY | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB Ready | [6 empty] | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_SB_ON_READY
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 8 |  | True | WTID_TECH_ROOM_ACCESS_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTID Technical Room Access Door |  |  |  | 531.1W0004 | 2x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTID_TECH_ROOM_ACCESS_DOOR
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 1 |  | True | WTID_FWD_CORRIDOR_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTID Fwd End Corridor Door |  |  |  | 531.1W0005 | 2x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTID_FWD_CORRIDOR_DOOR
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 2 |  | True | WTID_AFT_CORRIDOR_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTID Aft End corridor Door |  |  |  | 531.1W0006 | 2x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTID_AFT_CORRIDOR_DOOR
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 3 |  | True | WTSD_CLOSE_DOOR | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Close Door |  |  |  | 531.2W0003 | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTSD_CLOSE_DOOR | [17 empty] | False
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 4 |  | True | WTSD_MAIN_BACKUP_PWR_FAIL | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Man/Backup Power Failure |  |  |  |  | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTSD_MAIN_BACKUP_PWR_FAIL | [12 empty] | 366 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 5 |  | True | CLOSE_ALL_HULL_VALVES | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Close All Hull Valves From SOS Locker |  |  |  | 601W0034 | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.CLOSE_ALL_HULL_VALVES
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 6 |  | True | WTSD_DOOR_OPENED | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Door Opened |  |  |  | 531.2W0003 | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTSD_DOOR_OPENED
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 7 |  | True | WTSD_DOOR_CLOSED | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Door Closed |  |  |  |  | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTSD_DOOR_CLOSED
R2.2 |  | Bool | KEB2 | DI25 | 750-1415 | 8 |  | True | WTSD_LOW_AIR_PRESS | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | WTSD Low Air Pressure |  |  |  |  | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.WTSD_LOW_AIR_PRESS | [12 empty] | 370 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 1 |  | True | STEER_OIL_LEVEL_TOO_LOW | +CB.2 |  | 1000 | 170000 STEERING STYSTEM |  | Oil Level Too Low |  |  |  | 311W0011 | 7x2x0,75 |  | Mqtt1 | 170000 STEERING STYSTEM | $.STEER_OIL_LEVEL_TOO_LOW | [12 empty] | 371 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 2 |  | True | STEER_OIL_FILTER_CLOGGED | +CB.2 |  | 1000 | 170000 STEERING STYSTEM |  | Oil Filter Clogged | [6 empty] | Mqtt1 | 170000 STEERING STYSTEM | $.STEER_OIL_FILTER_CLOGGED | [12 empty] | 372 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 3 |  | True | STEER_24V_MONITORING | +CB.2 |  | 1000 | 170000 STEERING STYSTEM |  | 24 Voltage Monitoring | [6 empty] | Mqtt1 | 170000 STEERING STYSTEM | $.STEER_24V_MONITORING | [12 empty] | 373 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 4 |  | True | STEER_FREQ_DR_POWER_FAIL | +CB.2 |  | 1000 | 170000 STEERING STYSTEM |  | Frequency Drive Power Failure | [6 empty] | Mqtt1 | 170000 STEERING STYSTEM | $.STEER_FREQ_DR_POWER_FAIL | [12 empty] | 374 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 5 |  | True | DRAIN_VLV_Y02_POS_OVERBOARD | +CB.2 |  | 1000 | 250000 TECHWATER | 25004014_2 | Drain water Valve Y02 Position Overboard |  |  |  | 421.2W0049 | 7x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.DRAIN_VLV_Y02_POS_OVERBOARD
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 6 |  | True | DRAIN_VLV_Y02_POS_TO_PURO | +CB.2 |  | 1000 | 250000 TECHWATER | 25004014_2 | Drain water Valve Y02 Position to Puro | [6 empty] | Mqtt1 | 250000 TECHWATER | $.DRAIN_VLV_Y02_POS_TO_PURO
R1.12 |  | Bool | KEB2 | DI26 | 750-1415 | 7 |  | True | NOVEC_RELEASED_ALARM | +CB.2 |  | 1000 | 220000 NOVEC |  | Novec Released |  |  |  | 401.2W0004 | 2x2x0.75 |  | Mqtt1 | 220000 NOVEC | $.NOVEC_RELEASED_ALARM | [12 empty] | 377 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.12 | Connection drawings missing | Bool | KEB2 | DI26 | 750-1415 | 8 |  | True | NOVEC_BREAKER_TRIPPED_ALARM | +CB.2 |  | 1000 | 220000 NOVEC |  | Novec Breaker Tripped | [6 empty] | Mqtt1 | 220000 NOVEC | $.NOVEC_BREAKER_TRIPPED_ALARM | [12 empty] | 378 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 1 |  | True | SOS_LOCK_SUPPLY_14E1_1_Fail | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | SOS Locker Supply 14E1 1 Fail |  |  |  | 601W0033 | 4x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.SOS_LOCK_SUPPLY_14E1_1_Fail | [12 empty] | 379 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 2 |  | True | SOS_LOCK_SUPPLY_14E1_2_Fail | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | SOS Locker Supply 14E1 2 Fail |  |  |  |  | 4x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.SOS_LOCK_SUPPLY_14E1_2_Fail | [12 empty] | 380 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 3 |  | True | SOS_LOCK_SUPPLY_14E1_3_Fail | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | SOS Locker Supply 14E1 3 Fail |  |  |  |  | 4x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.SOS_LOCK_SUPPLY_14E1_3_Fail | [12 empty] | 381 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 4 |  | True | EMERG_STOP_MTS_VENT_ACTIVE | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop MTS Ventilation Active |  |  |  |  | 4x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.EMERG_STOP_MTS_VENT_ACTIVE | [12 empty] | 382 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 5 |  | True | EMERG_STOP_ACC_VENT_ACTIVE | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Accommodation Ventilation Active |  |  |  | 601W0034 | 7x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.EMERG_STOP_ACC_VENT_ACTIVE | [12 empty] | 383 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 6 |  | True | EMERG_STOP_GAL_VENT_ACTIVE | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Galley Ventilation Active | [6 empty] | Mqtt1 | 350000 VENTILATION | $.EMERG_STOP_GAL_VENT_ACTIVE | [12 empty] | 384 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI27 | 750-1415 | 7 |  | True | EMERG_STOP_HAZARDOUS_CONSUMERS | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Emergency Stop Hazardous Consumers Active | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.EMERG_STOP_HAZARDOUS_CONSUMERS | [12 empty] | 385 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.3 |  | Bool | KEB2 | DI27 | 750-1415 | 8 |  | True | STEER_FREQ_DR_FAIL | +CB.2 |  | 1000 | 170000 STEERING STYSTEM |  | Frequency Drive Power Failure |  |  |  | 311W0011 | 7x2x0,75 |  | Mqtt1 | 170000 STEERING STYSTEM | $.STEER_FREQ_DR_FAIL
R2.4 |  | Bool | KEB2 | DI28 | 750-1415 | 1 |  | True | GAS_DETECTION_LVL_SWITCH | +CB.2 |  | 1000 | 450000 GAS DETECTION |  | Gas Detection Level Switch Petrol Locker |  |  |  | 202W0002 | 2x2x0.75 |  | Mqtt1 | 450000 GAS DETECTION | $.GAS_DETECTION_LVL_SWITCH | [12 empty] | 387 |  |  |  |  | False |  | TS | BRG | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 2 |  | True | HELM_SB_OUT_DISP_ON_OFF | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB Out Display On/Off |  |  |  | 58A-C130 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_SB_OUT_DISP_ON_OFF
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 3 |  | True | HELM_SB_OUT_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB Out Display Toggle |  |  |  | 58A-C72 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_SB_OUT_DISP_TOGG
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 4 |  | True | HELM_SB_IN_DISP_ON_OFF | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB In Display On/Off |  |  |  | 58A-C130 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_SB_IN_DISP_ON_OFF
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 5 |  | True | HELM_SB_IN_DISP_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB In Display Toggle |  |  |  | 58A-C103 | CAT7 |  | Mqtt1 | KVM SWITCHING | $.HELM_SB_IN_DISP_TOGG
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 6 |  | True | HELM_SB_IN_DISP_AMCS | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB In Display AMCS Direct | [6 empty] | Mqtt1 | 450000 AMCS | $.HELM_SB_IN_DISP_AMCS
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 7 |  | True | HELM_SB_MUTE_AMCS | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB Mute AMCS |  |  |  | 601W0034 | 7x2x0,75 |  | Mqtt1 | 450000 AMCS | $.HELM_SB_MUTE_AMCS
R1.13 |  | Bool | KEB2 | DI28 | 750-1415 | 8 |  | True | HELM_SB_BACKLIGHT_UP_DOWN | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB Backlight Up/Down |  |  |  | 58A-C130 | CAT7 |  | Mqtt1 | 450000 AMCS | $.HELM_SB_BACKLIGHT_UP_DOWN
R1.13 |  | Bool | KEB2 | DI29 | 750-1415 | 1 |  | True | HELM_SB_CREW_CALL | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB Crew Call |  |  |  | ????? |  |  | Mqtt1 | 450000 AMCS | $.HELM_SB_CREW_CALL
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 2 |  | True | Spare_DI29_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 3 |  | True | Spare_DI29_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 4 |  | True | FWD_OXICELL_FIRE_FLAP_RELEASED | +CB.2 |  | 1000 | 350000 VENTILATION | 35005031_3 | FWD Space Oxycell Fire Flap Released |  |  |  | 415W0014 | 2x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.FWD_OXICELL_FIRE_FLAP_RELEASED | [12 empty] | 398 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Bool | KEB2 | DI29 | 750-1415 | 5 |  | True | FWD_OXYCELL_FIRE_FLAP_FULLY_RESET | +CB.2 |  | 1000 | 350000 VENTILATION | 35005031_3 | FWD Space Oxycell Fire Fire Flap Fully Reset | [6 empty] | Mqtt1 | 350000 VENTILATION | $.FWD_OXYCELL_FIRE_FLAP_FULLY_RESET | [12 empty] | 399 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.13 |  | Bool | KEB2 | DI29 | 750-1415 | 6 |  | True | GALLEY_HOOD_IN_FIRE_FLAP_RELEASED | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_1 | Galley Hood In Fire Flap Released |  |  |  | 415W0010 | 4x2x0.75 |  | Mqtt1 | 350000 VENTILATION | $.GALLEY_HOOD_IN_FIRE_FLAP_RELEASED | [12 empty] | 400 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.13 |  | Bool | KEB2 | DI29 | 750-1415 | 7 |  | True | GALLEY_HOOD_IN_FIRE_FLAP_FULLY_RESET | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_1 | Galley Hood In Fire Fire Flap Fully Reset | [6 empty] | Mqtt1 | 350000 VENTILATION | $.GALLEY_HOOD_IN_FIRE_FLAP_FULLY_RESET | [12 empty] | 401 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI29 | 750-1415 | 8 |  | True | GALLEY_HOOD_OUT_FIRE_FLAP_RELEASED | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_2 | Galley Hood Out Fire Flap Released | [6 empty] | Mqtt1 | 350000 VENTILATION | $.GALLEY_HOOD_OUT_FIRE_FLAP_RELEASED | [12 empty] | 402 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI30 | 750-1415 | 1 |  | True | GALLEY_HOOD_OUT_FIRE_FLAP_FULLY_RESET | +CB.2 |  | 1000 | 350000 VENTILATION | 35012001_2 | Galley Hood Out Fire Fire Flap Fully Reset | [6 empty] | Mqtt1 | 350000 VENTILATION | $.GALLEY_HOOD_OUT_FIRE_FLAP_FULLY_RESET | [12 empty] | 403 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.4 |  | Bool | KEB2 | DI30 | 750-1415 | 2 |  | True | W_TIGHT_DOOR_RM19_SEAL_INFLATED | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Door RM-19 Seal Inflated |  |  |  | 535.1W0029 | 2x2x0,75 |  | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_DOOR_RM19_SEAL_INFLATED
R2.4 |  | Bool | KEB2 | DI30 | 750-1415 | 3 |  | True | W_TIGHT_DOOR_RM19_DOOR_OPEN | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Door RM-19 Horizontal Hatch Closed | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_DOOR_RM19_DOOR_OPEN
R2.4 |  | Bool | KEB2 | DI30 | 750-1415 | 4 |  | True | W_TIGHT_DOOR_RM19_POS_PROG_SWITCH | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | Weather Tight Door RM-19 Vertical Hatch Closed | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.W_TIGHT_DOOR_RM19_POS_PROG_SWITCH
R2.6 |  | Bool | KEB2 | DI30 | 750-1415 | 5 |  | True | BURGLAR_ALARM_206U04 | +CB.2 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U04 |  |  |  | 601W0031 |  |  | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALARM_206U04
R2.6 |  | Bool | KEB2 | DI30 | 750-1415 | 6 |  | True | BURGLAR_ALARM_206U05 | +CB.2 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U05 | [6 empty] | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALARM_206U05
R2.6 |  | Bool | KEB2 | DI30 | 750-1415 | 7 |  | True | BURGLAR_ALARM_206U06 | +CB.2 |  | 1000 | 450000 BURGLAR |  | Burglar Alarm 206U06 | [6 empty] | Mqtt1 | 450000 BURGLAR | $.BURGLAR_ALARM_206U06
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 8 |  | True | Spare_DI30_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 1 |  | True | PCS_CB.11_COM_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Common Alarm |  |  |  | =16.12-W232 | 7x2x0,75 |  | Mqtt1 | 150000 PCS | $.PCS_CB.11_COM_ALARM | [12 empty] | 411 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  | 1 |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 2 |  | True | PCS_CB.11_24VDC_SERV_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 24Vdc Service Failure | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_24VDC_SERV_FAIL | [12 empty] | 412 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 3 |  | True | PCS_CB.11_24VDC_EMERG_FAIL | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 24Vdc Emergency Failure | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_24VDC_EMERG_FAIL | [12 empty] | 413 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 4 |  | True | PCS_CB.11_POWER_DISTR_INS | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Power Distribution Insulation | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_POWER_DISTR_INS | [12 empty] | 414 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 5 |  | True | PCS_CB.11_HYDR_PRESS_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Hydraulic Pressure Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_HYDR_PRESS_ALARM | [12 empty] | 415 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 6 |  | True | PCS_CB.11_OIL_LEV_ALARM_SEAL_TANK | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Oil level Alarm Shaft Seal Tank | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_OIL_LEV_ALARM_SEAL_TANK | [12 empty] | 416 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 7 |  | True | PCS_CB.11_GEAR_OIL_LEV_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Gear Oil Level Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_GEAR_OIL_LEV_ALARM | [12 empty] | 417 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI31 | 750-1415 | 8 |  | True | PCS_CB.11_GEAR_OIL_TEMP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Gear Oil Temperature Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_GEAR_OIL_TEMP_ALARM | [12 empty] | 418 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 1 |  | True | PCS_CB.11_OVERSP_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Overspeed Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_OVERSP_ALARM | [12 empty] | 419 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 2 |  | True | PCS_CB.11_OVERL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Overload Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_OVERL_ALARM | [12 empty] | 420 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 3 |  | True | PCS_CB.11_AZI_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Azimuth Follow Up Failure/Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_AZI_FOLL_UP_FAIL_ALARM | [12 empty] | 421 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.1 |  | Bool | KEB2 | DI32 | 750-1415 | 4 |  | True | PCS_CB.11_PITCH_FOLL_UP_FAIL_ALARM | +CB.1 |  | 1000 | 150000 PCS |  | PCS +CB.11 Thruster Pitch Follow Up Failure/Alarm | [6 empty] | Mqtt1 | 150000 PCS | $.PCS_CB.11_PITCH_FOLL_UP_FAIL_ALARM | [12 empty] | 422 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 5 |  | True | HVAC_SUPPLY_VALVE_2031_1_CLOSED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_1 | HVAC Supply Butterfly Valve 2031_1 Closed |  |  |  | 412.2W1253 | 7x2x0,75 |  | Mqtt1 | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_1_CLOSED
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 6 |  | True | HVAC_SUPPLY_VALVE_2031_1_OPENED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_1 | HVAC Supply Butterfly Valve 2031_1 Opened | [6 empty] | Mqtt1 | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_1_OPENED
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 7 |  | True | HVAC_SUPPLY_VALVE_2031_2_CLOSED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_2 | HVAC Supply Butterfly Valve 2031_2 Closed |  |  |  | 412.2W1259 | 7x2x0,75 |  | Mqtt1 | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_2_CLOSED
R2.6 |  | Bool | KEB2 | DI32 | 750-1415 | 8 |  | True | HVAC_SUPPLY_VALVE_2031_2_OPENED | +CB.2 |  | 1000 | 350000 VENTILATION | 35002031_2 | HVAC Supply Butterfly Valve 2031_2 Opened | [6 empty] | Mqtt1 | 350000 VENTILATION | $.HVAC_SUPPLY_VALVE_2031_2_OPENED
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 1 |  | True |  | +CB.2 |  | 1000 | SB HELM CONSOLE |  | SB Helm Notrot monitor DIM button |  |  |  | TEZ_58A-C130 |  |  | Mqtt1 | SB HELM CONSOLE | $.
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 2 |  | True | Spare_DI33_2 | +CB.2 |  | 1000 | SPARE |  | SB Helm Notrot monitor Toggle
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 3 |  | True | Spare_DI33_3 | +CB.2 |  | 1000 | SPARE |  | SB Helm Notrot monitor On/Off
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 4 |  | True | Spare_DI33_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 5 |  | True | Spare_DI33_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 6 |  | True | Spare_DI33_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 7 |  | True | Spare_DI33_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 8 |  | True | Spare_DI33_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 1 |  | True | Spare_DI34_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 2 |  | True | Spare_DI34_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 3 |  | True | Spare_DI34_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 4 |  | True | Spare_DI34_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 5 |  | True | Spare_DI34_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 6 |  | True | Spare_DI34_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 7 |  | True | Spare_DI34_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 8 |  | True | Spare_DI34_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 1 |  | True | Spare_DI35_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 2 |  | True | Spare_DI35_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 3 |  | True | Spare_DI35_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 4 |  | True | Spare_DI35_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 5 |  | True | Spare_DI35_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 6 |  | True | Spare_DI35_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 7 |  | True | Spare_DI35_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 8 |  | True | Spare_DI35_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 1 |  | True | Spare_DI36_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 2 |  | True | Spare_DI36_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 3 |  | True | Spare_DI36_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 4 |  | True | Spare_DI36_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 5 |  | True | Spare_DI36_5 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 6 |  | True | Spare_DI36_6 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 7 |  | True | Spare_DI36_7 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 8 |  | True | Spare_DI36_8 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.1 |  | Float | KEB2 | AI20 | 750-455 | 1 |  | True | CHAIN_LOCK_PRESS_SENSOR | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001049_1 | Chain Locker Bilge Level |  |  |  | 381W0048 | 2x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.CHAIN_LOCK_PRESS_SENSOR | [8 empty] | 0 | 1 | bar |  | 459 |  | 1 |  |  |  | 20 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 2 |  | True | BILGE_TANK_PRESS_SENSOR | +CB.2 |  | 1000 | 210000 BILGE FIFI | 21001050 | Bilge Tank Level |  |  |  | 381W0049 | 2x2x0,75 |  | Mqtt1 | 210000 BILGE FIFI | $.BILGE_TANK_PRESS_SENSOR | [8 empty] | 0 | 1 | bar |  | 460 |  | 1 |  |  |  | 20 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 3 |  | True | FLOW_CREW_MESS_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_18 | Flow Sensor Crew Mess Hot Water |  |  |  | 421.1W0106 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_MESS_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 4 |  | True | FLOW_CREW_MESS_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_17 | Flow Sensor Crew Mess Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_MESS_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 1 |  | True | FLOW_GALLEY_1_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_20 | Flow Sensor Galley 1 Hot Water |  |  |  | 421.1W0107 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_GALLEY_1_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 2 |  | True | FLOW_GALLEY_1_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_19 | Flow Sensor Galley 1 Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GALLEY_1_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 3 |  | True | FLOW_GALLEY_2_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_22 | Flow Sensor Galley 2 Hot Water |  |  |  | 421.1W0108 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_GALLEY_2_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 4 |  | True | FLOW_GALLEY_2_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_21 | Flow Sensor Galley 2 Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GALLEY_2_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 1 |  | True | FLOW_OVERFL_CABIN_BATHR_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_23 | Flow Sensor Overflow Cabin Bathroom Cold Water |  |  |  | 421.1W0109 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_OVERFL_CABIN_BATHR_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 2 |  | True | FLOW_GUEST_BATHR_PS_FWD_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_25 | Flow Sensor Guest Cabin Bathroom PS Fwd Hot Water |  |  |  | 421.1W0110 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_BATHR_PS_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 3 |  | True | FLOW_GUEST_BATHR_PS_FWD_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_24 | Flow Sensor Guest Cabin Bathroom PS Fwd Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_GUEST_BATHR_PS_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 4 |  | True | FLOW_LAUNDRY_PS_1_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_15 | Flow Sensor Laundry PS 1 Hot Water |  |  |  | 421.1W0111 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_LAUNDRY_PS_1_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 1 |  | True | FLOW_LAUNDRY_PS_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_14 | Flow Sensor Laundry PS Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_LAUNDRY_PS_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 2 |  | True | FLOW_LAUNDRY_PS_2_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_16 | Flow Sensor Laundry PS 2 Hot Water |  |  |  | 421.1W0112 | 4x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_LAUNDRY_PS_2_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI23 | 750-455 | 3 |  | True | FLOW_CAPTAINS_CABIN_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_13 | Flow Sensor Captains Cabin Hot Water |  |  |  | 601W0032 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_CAPTAINS_CABIN_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI23 | 750-455 | 4 |  | True | FLOW_CAPTAINS_CABIN_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_12 | Flow Sensor Captains Cabin Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CAPTAINS_CABIN_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 1 |  | True | FLOW_CREW_CABIN_SB_AFT_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_10 | Flow Sensor Crew Cabin SB Aft Hot Water |  |  |  | 601W0021 | 10x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_AFT_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 2 |  | True | FLOW_CREW_CABIN_SB_AFT_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_11 | Flow Sensor Crew Cabin SB Aft Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_AFT_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 3 |  | True | FLOW_CREW_CABIN_SB_MID_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_9 | Flow Sensor Crew Cabin SB Mid Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_MID_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI24 | 750-455 | 4 |  | True | FLOW_CREW_CABIN_SB_MID_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_8 | Flow Sensor Crew Cabin SB Mid Cold Water |  |  |  | 601W0032 | 19x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_MID_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 1 |  | True | FLOW_CREW_CABIN_PS_MID_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_7 | Flow Sensor Crew Cabin PS Mid Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_MID_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 2 |  | True | FLOW_CREW_CABIN_PS_MID_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_6 | Flow Sensor Crew Cabin PS Mid Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_MID_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 3 |  | True | FLOW_CREW_CABIN_SB_FWD_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_5 | Flow Sensor Crew Cabin SB Fwd Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI25 | 750-455 | 4 |  | True | FLOW_CREW_CABIN_SB_FWD_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_4 | Flow Sensor Crew Cabin SB Fwd Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_SB_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 1 |  | True | FLOW_CREW_CABIN_PS_FWD_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_3 | Flow Sensor Crew Cabin PS Fwd Hot Water |  |  |  | 601W0021 | 10x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_FWD_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 2 |  | True | FLOW_CREW_CABIN_PS_FWD_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_2 | Flow Sensor Crew Cabin PS Fwd Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_CREW_CABIN_PS_FWD_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 3 |  | True | FLOW_DECKHOUSE_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_28 | Flow Sensor Deckhouse Hot Water |  |  |  | 601W0023 | 14x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.FLOW_DECKHOUSE_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI26 | 750-455 | 4 |  | True | FLOW_DECKHOUSE_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_26 | Flow Sensor Deckhouse Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_DECKHOUSE_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI27 | 750-455 | 1 |  | True | FLOW_DECK_FR48_SB_TECH_COR_HOT_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_29 | Flow Sensor Deck Douche FR48 SB Technical Corridor Hot Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_DECK_FR48_SB_TECH_COR_HOT_WATER | [8 empty] | 0.05 | 35 | l/min
R2.2 |  | Float | KEB2 | AI27 | 750-455 | 2 |  | True | FLOW_DECK_FR48_SB_TECH_COR_COLD_WATER | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001037_27 | Flow Sensor Deck Douche FR48 SB Technical Corridor Cold Water | [6 empty] | Mqtt1 | 250000 FRESH WATER | $.FLOW_DECK_FR48_SB_TECH_COR_COLD_WATER | [8 empty] | 0.05 | 35 | l/min
R1.8 |  | Float | KEB2 | AI27 | 750-455 | 3 |  | True | PRESS_FR_46_SYSTEM_BEH_PRES_PUMPS | +CB.2 |  | 1000 | 250000 FRESH WATER | 25001036 | Pressure Sensor FR 46 System Pressure Behind Pressure Pumps |  |  |  | 421.1W0091 | 2x2x0,75 |  | Mqtt1 | 250000 FRESH WATER | $.PRESS_FR_46_SYSTEM_BEH_PRES_PUMPS | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI27 | 750-455 | 4 |  | True | ACC_SENSOR_1_OUTPX | +CB.2 |  | 1000 | 450000 AMCS | 45019001_1 | Acceleration Sensor 1 Output X |  |  |  | 615.2W0003 | 14x2x0,75 |  | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_1_OUTPX | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 1 |  | True | ACC_SENSOR_1_OUTPY | +CB.2 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 1 Output Y | [6 empty] | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_1_OUTPY | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 2 |  | True | ACC_SENSOR_1_OUTPZ | +CB.2 |  | 1000 | 450000 AMCS |  | Acceleration Sensor 1 Output Z | [6 empty] | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_1_OUTPZ | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 3 |  | True | LEVEL_GREY_WATER_TANK_FWD_SB | +CB.2 |  | 1000 | 340000 SEWAGE | 34001025_4 | Level Sensor Grey Water Tank Fwd FR 33 SB |  |  |  | 601W0028 | 10x2x0,75 |  | Mqtt1 | 340000 SEWAGE | $.LEVEL_GREY_WATER_TANK_FWD_SB | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI28 | 750-455 | 4 |  | True | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B05 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004037_2 | Flow Sensor Reel For Deckwash B05 |  |  |  | 601W0021 | 2x2x0.75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_REEL_FOR_DECKWASH_B05 | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI29 | 750-455 | 1 |  | True | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B06 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004037_3 | Flow Sensor Reel For Deckwash B06 | [6 empty] | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_REEL_FOR_DECKWASH_B06 | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI29 | 750-455 | 2 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B07 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004034_2 | Flow Sensor Adiabatic Cooling Line B07 |  |  |  | 601W0029 | 14x2x0,75 |  | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_ADIABATIC_COOL_B07 | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI29 | 750-455 | 3 |  | True | TECH_WAT_FLOW_ADIABATIC_COOL_B08 | +CB.2 |  | 1000 | 250000 TECHWATER | 25004034_3 | Flow Sensor Adiabatic Cooling Line B08 | [6 empty] | Mqtt1 | 250000 TECHWATER | $.TECH_WAT_FLOW_ADIABATIC_COOL_B08 | [8 empty] | 4 | 20 | 4-20mA
R2.4 |  | Float | KEB2 | AI29 | 750-455 | 4 |  | True | DAS_DETECTION_PERCT | +CB.2 |  | 1000 | 450000 GAS DETECTION |  | Gas Detection Percentage Petrol Locker |  |  |  | 202W0002 | 2x2x0.75 |  | Mqtt1 | 450000 GAS DETECTION | $.DAS_DETECTION_PERCT | [8 empty] | 4 | 20 | 4-20mA
R2.2 |  | Float | KEB2 | AI30 | 750-450 | 1 |  | True | BOW_THRUST_BEARING_TEMP_DE | +CB.2 |  | 1000 | 150000 PROPULSION |  | Fwd Thrust Motor Bearing Temperature DE |  |  |  | 13.31-W130 | 8x2x0.75 |  | Mqtt1 | 150000 PROPULSION | $.BOW_THRUST_BEARING_TEMP_DE | [8 empty] | 0 | 150 | °C |  | 499 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB2 | AI30 | 750-450 | 2 |  | True | BOW_THRUST_BEARING_TEMP_NDE | +CB.2 |  | 1000 | 150000 PROPULSION |  | Fwd Thrust Motor Bearing Temperature NDE | [6 empty] | Mqtt1 | 150000 PROPULSION | $.BOW_THRUST_BEARING_TEMP_NDE | [8 empty] | 0 | 150 | °C |  | 500 | 90 | 80 |  |  |  |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.12 |  | Float | KEB2 | AI30 | 750-450 | 3 |  | True | CABINET_INTERNAL_TEMP | +CB.2 |  | 1000 | 450000 AMCS |  | Cabinet Internal Temperature Measurement |  |  |  | INTERNAL |  |  | Mqtt1 | 450000 AMCS | $.CABINET_INTERNAL_TEMP | [8 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI30 | 750-450 | 4 |  | True | Spare_AI30_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [17 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 1 |  | True | Spare_AI31_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [17 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 2 |  | True | Spare_AI31_2 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [17 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 3 |  | True | Spare_AI31_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [17 empty] | 4 | 20 | °C
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 4 |  | True | Spare_AI31_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [17 empty] | 4 | 20 | °C
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 1 |  | True | AmcsPlcPowerModule2FuseBlown | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 2 Fuse Blown | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule2FuseBlown | [12 empty] | 507 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 2 |  | True | AmcsPlcPowerModule2PowerFailure | +CB.2 |  | 1000 | 450000 AMCS |  | AMCS PLC KEB2 Power Module 2 Power Failure | [6 empty] | Mqtt1 | 450000 AMCS | $.AmcsPlcPowerModule2PowerFailure | [12 empty] | 508 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R2.2 |  | Float | KEB2 | AO60 | 750-555 | 1 |  | True | BATT_VENT_AFT_PS_SPEED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD PS Speed |  |  |  | 412.3W0010 | 7x2x0,75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_AFT_PS_SPEED | [8 empty] | 0 | 100 | %
R2.2 |  | Float | KEB2 | AO60 | 750-555 | 2 |  | True | BATT_VENT_FWD_SB_SPEED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Battery Ventilation FWD SB Speed |  |  |  | 412.3W0011 | 7x2x0,75 |  | Mqtt1 | 350000 VENTILATION | $.BATT_VENT_FWD_SB_SPEED | [8 empty] | 0 | 100 | %
R0.1 |  | Float | KEB2 | AO60 | 750-555 | 3 |  | True | Spare_AO60_3 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [19 empty] | na
R0.1 |  | Float | KEB2 | AO60 | 750-555 | 4 |  | True | Spare_AO60_4 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2 | [19 empty] | na
R2.3 |  | Bool | KEB2 | DO60 | 750-1500 | 1 |  | True | Spare_DO60_1 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.2 |  | Bool | KEB2 | DO60 | 750-1500 | 2 |  | True | HULL_VALVES_ALL_CLOSED_GREEN | +CB.2 |  | 1000 | 090000 DOORS HATCHES |  | All Hull Valves Closed (Green Pilot Light) |  |  |  | 601W0034 | 7x2x0.75 |  | Mqtt1 | 090000 DOORS HATCHES | $.HULL_VALVES_ALL_CLOSED_GREEN
R2.2 |  | Bool | KEB2 | DO60 | 750-1500 | 3 |  | True | HULL_VALVES_OPEN_RED | #NAME? |  | 1000 | 090000 DOORS HATCHES |  | Not All Hull Valves Closed (Red Pilot Light) | [6 empty] | Mqtt1 | 090000 DOORS HATCHES | $.HULL_VALVES_OPEN_RED
R1.12 |  | Bool | KEB2 | DO60 | 750-1500 | 4 |  | True | CABINET_INTERNAL_FAN_CONTROL | +CB.2 |  | 1000 | 450000 AMCS |  | Cabinet Internal Fan Control |  |  |  | INTERNAL |  |  | Mqtt1 | 450000 AMCS | $.CABINET_INTERNAL_FAN_CONTROL
R2.3 |  | Bool | KEB2 | DO60 | 750-1500 | 5 |  | True | SEA_WATER_COOL_PMP2_START_STOP | +CB.2 |  | 1000 | 380000 SEAWATER |  | Sea Water Cooling Pump 2 Start/Stop |  |  |  | 373W0028 | 4x2x0,75 |  | Mqtt1 | 380000 SEAWATER | $.SEA_WATER_COOL_PMP2_START_STOP
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 6 |  | True | HELM_SB_IN_MOUSE_TOGG | +CB.2 |  | 1000 | KVM SWITCHING |  | Helmstation SB In Mouse Toggle |  |  |  | 58A-C154 | 2x2x0.5 |  | Mqtt1 | KVM SWITCHING | $.HELM_SB_IN_MOUSE_TOGG
R2.2 |  | Bool | KEB2 | DO60 | 750-1500 | 7 |  | True | ACC_SENSOR_ZEROING_2 | +CB.2 |  | 1000 | 450000 AMCS |  | Zeroing acc Sensor 2 |  |  |  | 601W0030 | 14x2x0.75 |  | Mqtt1 | 450000 AMCS | $.ACC_SENSOR_ZEROING_2
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 8 |  | True | HELM_SB_AMCS_MUTE_FB | +CB.2 |  | 1000 | 450000 AMCS |  | Helmstation SB AMCS Mute Feedback |  |  |  | ???? |  |  | Mqtt1 | 450000 AMCS | $.HELM_SB_AMCS_MUTE_FB
R2.1 |  | Bool | KEB2 | DO60 | 750-1500 | 9 |  | True | Spare_DO60_9 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R2.1 |  | Bool | KEB2 | DO60 | 750-1500 | 10 |  | True | Spare_DO60_10 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 11 |  | True | EMERG_STOP_ACC_VENT_ACTIVATED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Accommodation Ventilation Activated |  |  |  | ???? |  |  | Mqtt1 | 350000 VENTILATION | $.EMERG_STOP_ACC_VENT_ACTIVATED
R1.13 |  | Bool | KEB2 | DO60 | 750-1500 | 12 |  | True | EMERG_STOP_GAL_VENT_ACTIVATED | +CB.2 |  | 1000 | 350000 VENTILATION |  | Emergency Stop Galley Ventilation Activated |  |  |  | ???? |  |  | Mqtt1 | 350000 VENTILATION | $.EMERG_STOP_GAL_VENT_ACTIVATED
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 13 |  | True | Spare_DO60_13 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 14 |  | True | Spare_DO60_14 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 15 |  | True | Spare_DO60_15 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 16 |  | True | Spare_DO60_16 | +CB.2 |  | 1000 | SPARE |  | Spare Yard _True_+CB.2
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port1
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port2
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port3
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC2 Port4
| True | [10 empty] | 1000 |  |  | Serial Interface - KEC3 Port1
R1.9 |  | Bool | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Hoistable Anchor FWD Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Hoistable_Anchor_FwdStatus | 1 | Coil | 0
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | Coil | 1
R1.9 |  | Bool | NavLights |  |  |  |  | True | Starboard_BowStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Starboard BOW Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Starboard_BowStatus | 1 | Coil | 2
R1.9 |  | Bool | NavLights |  |  |  |  | True | Portside_BowStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Portside BOW Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Portside_BowStatus | 1 | Coil | 3
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | SB Nav. Spr. (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.SB_Nav_Spr_MAINStatus | 1 | Coil | 4
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | SB Nav. Spr. (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.SB_Nav_Spr_BACKUPStatus | 1 | Coil | 5
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PS Nav. Spr. (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PS_Nav_Spr_MAINStatus | 1 | Coil | 6
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PS Nav. Spr. (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PS_Nav_Spr_BACKUPStatus | 1 | Coil | 7
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Anchor AFT (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Anchor_Aft_MAINStatus | 1 | Coil | 8
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Anchor AFT (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Anchor_Aft_BACKUPStatus | 1 | Coil | 9
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Main (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Main_MAINStatus | 1 | Coil | 10
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Main (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Main_BACKUPStatus | 1 | Coil | 11
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Mizz. (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Mizz_MAINStatus | 1 | Coil | 12
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Mizz. (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Mizz_BACKUPStatus | 1 | Coil | 13
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC SB 180° (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_SB180_MAINStatus | 1 | Coil | 14
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC SB 180° (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_SB180_BACKUPStatus | 1 | Coil | 15
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC PS 180° (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_PS180_MAINStatus | 1 | Coil | 16
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC PS180° (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_PS180_BACKUPStatus | 1 | Coil | 17
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing SB 180° (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_SB180_MAINStatus | 1 | Coil | 18
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing SB 180° (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_SB180_BACKUPStatus | 1 | Coil | 19
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing PS 180° (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_PS180_MAINStatus | 1 | Coil | 20
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing PS 180° (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_PS180_BACKUPStatus | 1 | Coil | 21
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC & Sailing (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_and_Sailing_MAINStatus | 1 | Coil | 22
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC & Sailing (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_and_Sailing_BACKUPStatus | 1 | Coil | 23
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_MAINStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Stern (MAIN) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Stern_MAINStatus | 1 | Coil | 24
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_BACKUPStatus | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Stern (BACKUP) Status | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Stern_BACKUPStatus | 1 | Coil | 25
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | Coil | 26
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | Coil | 27
R1.9 |  | Bool | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Hoistable Anchor FWD Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Hoistable_Anchor_FwdCtrl | 1 | Coil | 300
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | Coil | 301
R1.9 |  | Bool | NavLights |  |  |  |  | True | Starboard_BowCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Starboard BOW Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Starboard_BowCtrl | 1 | Coil | 302
R1.9 |  | Bool | NavLights |  |  |  |  | True | Portside_BowCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Portside BOW Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Portside_BowCtrl | 1 | Coil | 303
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | SB Nav. Spr. (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.SB_Nav_Spr_MAINCtrl | 1 | Coil | 304
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | SB Nav. Spr. (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.SB_Nav_Spr_BACKUPCtrl | 1 | Coil | 305
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PS Nav. Spr. (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PS_Nav_Spr_MAINCtrl | 1 | Coil | 306
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PS Nav. Spr. (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PS_Nav_Spr_BACKUPCtrl | 1 | Coil | 307
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Anchor AFT (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Anchor_Aft_MAINCtrl | 1 | Coil | 308
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Anchor AFT (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Anchor_Aft_BACKUPCtrl | 1 | Coil | 309
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Main (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Main_MAINCtrl | 1 | Coil | 310
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Main (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Main_BACKUPCtrl | 1 | Coil | 311
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Mizz. (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Mizz_MAINCtrl | 1 | Coil | 312
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Mizz. (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Mizz_BACKUPCtrl | 1 | Coil | 313
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC SB 180° (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_SB180_MAINCtrl | 1 | Coil | 314
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC SB 180° (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_SB180_BACKUPCtrl | 1 | Coil | 315
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC PS 180° (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_PS180_MAINCtrl | 1 | Coil | 316
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC PS 180° (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_PS180_BACKUPCtrl | 1 | Coil | 317
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing SB 180° (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_SB180_MAINCtrl | 1 | Coil | 318
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing SB 180° (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_SB180_BACKUPCtrl | 1 | Coil | 319
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing PS 180° (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_PS180_MAINCtrl | 1 | Coil | 320
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing PS 180° (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_PS180_BACKUPCtrl | 1 | Coil | 321
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC & Sailing (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_and_Sailing_MAINCtrl | 1 | Coil | 322
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC & Sailing (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_and_Sailing_BACKUPCtrl | 1 | Coil | 323
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_MAINCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Stern (MAIN) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Stern_MAINCtrl | 1 | Coil | 324
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_BACKUPCtrl | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Stern (BACKUP) Control | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Stern_BACKUPCtrl | 1 | Coil | 325
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | Coil | 326
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | Coil | 327
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerMainOn | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PowerMainOn | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PowerMainOn | 1 | Coil | 1000
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerEmergencyOn | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PowerEmergencyOn | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PowerEmergencyOn | 1 | Coil | 1001
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerLampsOn | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PowerLampsOn | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PowerLampsOn | 1 | Coil | 1002
R1.9 |  | Bool | NavLights |  |  |  |  | True | ManualOperationActive | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | ManualOperationActive | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.ManualOperationActive | 1 | Coil | 1003
R1.9 |  | Bool | NavLights |  |  |  |  | True | CommunicationError | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | CommunicationError | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.CommunicationError | 1 | Coil | 2000
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Hoistable Anchor FWD Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Hoistable_Anchor_FwdOpTime | 1 | HoldingRegister | 40000 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | HoldingRegister | 40002 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Starboard_BowOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Starboard BOW Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Starboard_BowOpTime | 1 | HoldingRegister | 40004 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Portside_BowOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Portside BOW Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Portside_BowOpTime | 1 | HoldingRegister | 40006 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | SB Nav. Spr. (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.SB_Nav_Spr_MAINOpTime | 1 | HoldingRegister | 40008 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | SB Nav. Spr. (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.SB_Nav_Spr_BACKUPOpTime | 1 | HoldingRegister | 40010 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PS Nav. Spr. (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PS_Nav_Spr_MAINOpTime | 1 | HoldingRegister | 40012 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | PS Nav. Spr. (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.PS_Nav_Spr_BACKUPOpTime | 1 | HoldingRegister | 40014 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Anchor_Aft_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Anchor AFT (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Anchor_Aft_MAINOpTime | 1 | HoldingRegister | 40016 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Anchor AFT (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Anchor_Aft_BACKUPOpTime | 1 | HoldingRegister | 40018 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Main_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Main (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Main_MAINOpTime | 1 | HoldingRegister | 40020 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Main_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Main (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Main_BACKUPOpTime | 1 | HoldingRegister | 40022 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Mizz_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Mizz. (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Mizz_MAINOpTime | 1 | HoldingRegister | 40024 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Steam. Mizz. (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Steam_Mizz_BACKUPOpTime | 1 | HoldingRegister | 40026 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_SB180_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC Stb180° (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_SB180_MAINOpTime | 1 | HoldingRegister | 40028 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_SB180_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC Stb180° (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_SB180_BACKUPOpTime | 1 | HoldingRegister | 40030 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_PS180_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC PS 180° (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_PS180_MAINOpTime | 1 | HoldingRegister | 40032 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_PS180_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC PS 180° (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_PS180_BACKUPOpTime | 1 | HoldingRegister | 40034 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_SB180_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing SB 180° (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_SB180_MAINOpTime | 1 | HoldingRegister | 40036 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing SB 180° (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_SB180_BACKUPOpTime | 1 | HoldingRegister | 40038 | [7 empty] | Minutes
R1.10 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_PS180_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing PS 180° (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_PS180_MAINOpTime | 1 | HoldingRegister | 40040 | [7 empty] | Minutes
R1.10 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Sailing PS 180° (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Sailing_PS180_BACKUPOpTime | 1 | HoldingRegister | 40042 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC & Sailing (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_and_Sailing_MAINOpTime | 1 | HoldingRegister | 40044 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | NUC & Sailing (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.NUC_and_Sailing_BACKUPOpTime | 1 | HoldingRegister | 40046 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Stern_MAINOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Stern (MAIN) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Stern_MAINOpTime | 1 | HoldingRegister | 40048 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Stern_BACKUPOpTime | +CB.2 |  | 1000 | NAVIGATION LIGHTS |  | Stern (BACKUP) Operating Time | [6 empty] | Mqtt1 | NAVIGATION LIGHTS | $.Stern_BACKUPOpTime | 1 | HoldingRegister | 40050 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | HoldingRegister | 40052 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 |  | 1000 | SPARE |  | SPARE | [9 empty] | 1 | HoldingRegister | 40054 | [7 empty] | Minutes
| True | [13 empty] | Serial Interface - AC Breakers +10P0.1 - AC DISTRIBUTION BOARD 400/230V PANEL 1
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Voltage_ A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Voltage_ B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_RMS_Voltage_ C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT109F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Iridium GMDSS Supply Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT109F01_Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Voltage_ A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Voltage_ B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_RMS_Voltage_ C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT129F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit Offline Filter Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT129F01_Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Voltage_ A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Voltage_ B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_RMS_Voltage_ C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT130F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT130F01_Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Voltage_ A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Voltage_ B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_RMS_Voltage_ C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT132F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | EREC 1 Power Supply Heat Recovery Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT132F01_Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Voltage_ A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Voltage_ B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_RMS_Voltage_ C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Owners State Room Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135F01_Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Voltage_ A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Voltage_ B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_RMS_Voltage_ C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating ACtive Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating ACtive Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating ACtive Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating Total ACtive Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT137F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Propulsion Unit AC Heating Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT137F01_Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Voltage_ A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Voltage_ B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_RMS_Voltage_ C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT138F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Potable Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT138F01_Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Voltage_ A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Voltage_ B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_RMS_Voltage_ C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT139F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 1 PS Deck Locker Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT139F01_Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Voltage_ A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Voltage_ B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_RMS_Voltage_ C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT140F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Drain Pump 3 PS Deck Locker Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT140F01_Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Voltage_ A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Voltage_ B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_RMS_Voltage_ C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT141F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Bilge Water Separator Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT141F01_Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Voltage_ A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Voltage_ B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_RMS_Voltage_ C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT142F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT142F01_Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Voltage_ A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Voltage_ B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_RMS_Voltage_ C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT143F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT143F01_Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Voltage_ A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Voltage_ B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_RMS_Voltage_ C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT144F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT144F01_Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Voltage_ A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Voltage_ B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_RMS_Voltage_ C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT145F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Draink Tank Mast Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT145F01_Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Voltage_ A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Voltage_ B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_RMS_Voltage_ C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT146F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Watermaker Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT146F01_Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Voltage_ A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Voltage_ B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_RMS_Voltage_ C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT147F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pumps Aft Technical Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT147F01_Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Voltage_ A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Voltage_ B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_RMS_Voltage_ C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT148F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Co2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT148F01_Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Voltage_ A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Voltage_ B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_RMS_Voltage_ C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT149F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Antifouling System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT149F01_Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Voltage_ A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Voltage_ B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_RMS_Voltage_ C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT150F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT150F01_Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Voltage_ A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Voltage_ B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_RMS_Voltage_ C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT152F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT152F01_Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Voltage_ A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Voltage_ B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_RMS_Voltage_ C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT153F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Hydrophore 1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT153F01_Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Voltage_ A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Voltage_ B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_RMS_Voltage_ C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT154F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump Adiabtic Pump Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT154F01_Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Voltage_ A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Voltage_ B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_RMS_Voltage_ C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT161F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Main Salon JB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT161F01_Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Voltage_ A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Voltage_ B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_RMS_Voltage_ C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT164F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Distrbution Panel 115V Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT164F01_Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Voltage_ A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Voltage_ B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_RMS_Voltage_ C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT165F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Master Cabin PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT165F01_Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Voltage_ A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Voltage_ B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_RMS_Voltage_ C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT166F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT166F01_Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Voltage_ A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Voltage_ B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_RMS_Voltage_ C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT167F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Guest PS And Overflow Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT167F01_Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Voltage_ A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Voltage_ B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_RMS_Voltage_ C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT168F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Charger Radio Batteries (GMDSS) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT168F01_Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Voltage_ A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Voltage_ B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_RMS_Voltage_ C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT169F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 1) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT169F01_Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Voltage_ A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Voltage_ B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_RMS_Voltage_ C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT170F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Underwater Lights PS (Group 2) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT170F01_Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Voltage_ A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Voltage_ B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_RMS_Voltage_ C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT171F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU EXH2000 Above Laundry Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT171F01_Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Voltage_ A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Voltage_ B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_RMS_Voltage_ C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT172F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Discharge Pump Galley/Crew Mess Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT172F01_Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Current_Phase_A | 33 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Current_Phase_B | 33 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Current_Phase_C | 33 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Current_Phase_Neut | 33 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Voltage_ A_N | 33 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Voltage_ B_N | 33 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_RMS_Voltage_ C_N | 33 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Active_Power_Phase_A | 33 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Active_Power_Phase_B | 33 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Active_Power_Phase_C | 33 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Total_Active_Power | 33 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Power_Factor_Phase_A | 33 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Power_Factor_Phase_B | 33 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Power_Factor_Phase_C | 33 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT175F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Ship Office Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT175F01_Total_Power_Factor | 33 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Current_Phase_A | 34 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Current_Phase_B | 34 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Current_Phase_C | 34 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Current_Phase_Neut | 34 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Voltage_ A_N | 34 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Voltage_ B_N | 34 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_RMS_Voltage_ C_N | 34 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Active_Power_Phase_A | 34 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Active_Power_Phase_B | 34 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Active_Power_Phase_C | 34 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Total_Active_Power | 34 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Power_Factor_Phase_A | 34 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Power_Factor_Phase_B | 34 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Power_Factor_Phase_C | 34 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT176F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Display Switching Supply Helm PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT176F01_Total_Power_Factor | 34 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Current_Phase_A | 35 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Current_Phase_B | 35 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Current_Phase_C | 35 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Current_Phase_Neut | 35 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Voltage_ A_N | 35 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Voltage_ B_N | 35 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_RMS_Voltage_ C_N | 35 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Active_Power_Phase_A | 35 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Active_Power_Phase_B | 35 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Active_Power_Phase_C | 35 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Total_Active_Power | 35 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Power_Factor_Phase_A | 35 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Power_Factor_Phase_B | 35 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Power_Factor_Phase_C | 35 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT177F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | ECDIS 1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT177F01_Total_Power_Factor | 35 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Current_Phase_A | 36 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Current_Phase_B | 36 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Current_Phase_C | 36 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Current_Phase_Neut | 36 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Voltage_ A_N | 36 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Voltage_ B_N | 36 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_RMS_Voltage_ C_N | 36 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Active_Power_Phase_A | 36 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Active_Power_Phase_B | 36 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Active_Power_Phase_C | 36 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Total_Active_Power | 36 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Power_Factor_Phase_A | 36 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Power_Factor_Phase_B | 36 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Power_Factor_Phase_C | 36 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT178F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Radar 1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT178F01_Total_Power_Factor | 36 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Current_Phase_A | 37 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Current_Phase_B | 37 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Current_Phase_C | 37 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Current_Phase_Neut | 37 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Voltage_ A_N | 37 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Voltage_ B_N | 37 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_RMS_Voltage_ C_N | 37 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Active_Power_Phase_A | 37 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Active_Power_Phase_B | 37 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Active_Power_Phase_C | 37 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Total_Active_Power | 37 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Power_Factor_Phase_A | 37 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Power_Factor_Phase_B | 37 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Power_Factor_Phase_C | 37 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT179F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Speedlog Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT179F01_Total_Power_Factor | 37 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Current_Phase_A | 38 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Current_Phase_B | 38 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Current_Phase_C | 38 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Current_Phase_Neut | 38 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Voltage_ A_N | 38 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Voltage_ B_N | 38 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_RMS_Voltage_ C_N | 38 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Active_Power_Phase_A | 38 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Active_Power_Phase_B | 38 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Active_Power_Phase_C | 38 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Total_Active_Power | 38 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Power_Factor_Phase_A | 38 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Power_Factor_Phase_B | 38 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Power_Factor_Phase_C | 38 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT180F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | VHF 1 (Main) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT180F01_Total_Power_Factor | 38 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Current_Phase_A | 39 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Current_Phase_B | 39 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Current_Phase_C | 39 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Current_Phase_Neut | 39 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Voltage_ A_N | 39 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Voltage_ B_N | 39 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_RMS_Voltage_ C_N | 39 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Active_Power_Phase_A | 39 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Active_Power_Phase_B | 39 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Active_Power_Phase_C | 39 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Total_Active_Power | 39 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Power_Factor_Phase_A | 39 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Power_Factor_Phase_B | 39 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Power_Factor_Phase_C | 39 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT181F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | AHU Technical Room Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT181F01_Total_Power_Factor | 39 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Current_Phase_A | 40 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Current_Phase_B | 40 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Current_Phase_C | 40 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Current_Phase_Neut | 40 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Voltage_ A_N | 40 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Voltage_ B_N | 40 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_RMS_Voltage_ C_N | 40 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Active_Power_Phase_A | 40 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Active_Power_Phase_B | 40 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Active_Power_Phase_C | 40 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Total_Active_Power | 40 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Power_Factor_Phase_A | 40 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Power_Factor_Phase_B | 40 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Power_Factor_Phase_C | 40 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT182F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Central Panel Smart Ventilation System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT182F01_Total_Power_Factor | 40 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Current_Phase_A | 41 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Current_Phase_B | 41 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Current_Phase_C | 41 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Current_Phase_Neut | 41 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Voltage_ A_N | 41 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Voltage_ B_N | 41 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_RMS_Voltage_ C_N | 41 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Active_Power_Phase_A | 41 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Active_Power_Phase_B | 41 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Active_Power_Phase_C | 41 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Total_Active_Power | 41 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Power_Factor_Phase_A | 41 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Power_Factor_Phase_B | 41 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Power_Factor_Phase_C | 41 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT183F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | BNWAS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT183F01_Total_Power_Factor | 41 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Current_Phase_A | 42 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Current_Phase_B | 42 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Current_Phase_C | 42 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Current_Phase_Neut | 42 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Voltage_ A_N | 42 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Voltage_ B_N | 42 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_RMS_Voltage_ C_N | 42 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Active_Power_Phase_A | 42 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Active_Power_Phase_B | 42 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Active_Power_Phase_C | 42 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Total_Active_Power | 42 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Power_Factor_Phase_A | 42 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Power_Factor_Phase_B | 42 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Power_Factor_Phase_C | 42 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT184F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | GPS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT184F01_Total_Power_Factor | 42 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Current_Phase_A | 43 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Current_Phase_B | 43 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Current_Phase_C | 43 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Current_Phase_Neut | 43 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Voltage_ A_N | 43 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Voltage_ B_N | 43 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_RMS_Voltage_ C_N | 43 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Active_Power_Phase_A | 43 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Active_Power_Phase_B | 43 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Active_Power_Phase_C | 43 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Locker Ventilation Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Total_Active_Power | 43 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Power_Factor_Phase_A | 43 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Power_Factor_Phase_B | 43 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Power_Factor_Phase_C | 43 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT186F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT186F01_Total_Power_Factor | 43 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Current_Phase_A | 44 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Current_Phase_B | 44 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Current_Phase_C | 44 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Current_Phase_Neut | 44 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Voltage_ A_N | 44 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Voltage_ B_N | 44 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_RMS_Voltage_ C_N | 44 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Active_Power_Phase_A | 44 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Active_Power_Phase_B | 44 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Active_Power_Phase_C | 44 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Peplink 5G Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Total_Active_Power | 44 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Power_Factor_Phase_A | 44 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Power_Factor_Phase_B | 44 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Power_Factor_Phase_C | 44 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT201F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT201F01_Total_Power_Factor | 44 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Current_Phase_A | 45 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Current_Phase_B | 45 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Current_Phase_C | 45 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Current_Phase_Neut | 45 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Voltage_ A_N | 45 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Voltage_ B_N | 45 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_RMS_Voltage_ C_N | 45 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Active_Power_Phase_A | 45 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Active_Power_Phase_B | 45 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Active_Power_Phase_C | 45 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Total_Active_Power | 45 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Power_Factor_Phase_A | 45 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Power_Factor_Phase_B | 45 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Power_Factor_Phase_C | 45 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT110Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Transfer Pump 1 Grey/Black Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT110Q01_Total_Power_Factor | 45 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Current_Phase_A | 46 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Current_Phase_B | 46 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Current_Phase_C | 46 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Current_Phase_Neut | 46 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Voltage_ A_N | 46 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Voltage_ B_N | 46 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_RMS_Voltage_ C_N | 46 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Active_Power_Phase_A | 46 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Active_Power_Phase_B | 46 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Active_Power_Phase_C | 46 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Total_Active_Power | 46 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Power_Factor_Phase_A | 46 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Power_Factor_Phase_B | 46 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Power_Factor_Phase_C | 46 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT116Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump System Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT116Q01_Total_Power_Factor | 46 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Current_Phase_A | 47 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Current_Phase_B | 47 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Current_Phase_C | 47 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Current_Phase_Neut | 47 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Voltage_ A_N | 47 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Voltage_ B_N | 47 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_RMS_Voltage_ C_N | 47 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Active_Power_Phase_A | 47 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Active_Power_Phase_B | 47 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Active_Power_Phase_C | 47 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Total_Active_Power | 47 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Power_Factor_Phase_A | 47 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Power_Factor_Phase_B | 47 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Power_Factor_Phase_C | 47 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT117Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Sea Water Cooling Pump 1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT117Q01_Total_Power_Factor | 47 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Current_Phase_A | 48 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Current_Phase_B | 48 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Current_Phase_C | 48 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Current_Phase_Neut | 48 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Voltage_ A_N | 48 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Voltage_ B_N | 48 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_RMS_Voltage_ C_N | 48 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Active_Power_Phase_A | 48 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Active_Power_Phase_B | 48 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Active_Power_Phase_C | 48 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Total_Active_Power | 48 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Power_Factor_Phase_A | 48 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Power_Factor_Phase_B | 48 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Power_Factor_Phase_C | 48 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT131Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Technical Space Ventilator - In Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT131Q01_Total_Power_Factor | 48 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Current_Phase_A | 49 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Current_Phase_B | 49 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Current_Phase_C | 49 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Current_Phase_Neut | 49 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Voltage_ A_N | 49 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Voltage_ B_N | 49 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_RMS_Voltage_ C_N | 49 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Active_Power_Phase_A | 49 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Active_Power_Phase_B | 49 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Active_Power_Phase_C | 49 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Total_Active_Power | 49 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Power_Factor_Phase_A | 49 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Power_Factor_Phase_B | 49 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Power_Factor_Phase_C | 49 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT133Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Fresh Air Unit Aft Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT133Q01_Total_Power_Factor | 49 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Current_Phase_A | 50 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Current_Phase_B | 50 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Current_Phase_C | 50 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Current_Phase_Neut | 50 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Voltage_ A_N | 50 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Voltage_ B_N | 50 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_RMS_Voltage_ C_N | 50 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Active_Power_Phase_A | 50 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Active_Power_Phase_B | 50 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Active_Power_Phase_C | 50 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Total_Active_Power | 50 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Power_Factor_Phase_A | 50 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Power_Factor_Phase_B | 50 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Power_Factor_Phase_C | 50 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT134Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Extraction Unit Aft Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT134Q01_Total_Power_Factor | 50 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Current_Phase_A | 51 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Current_Phase_B | 51 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Current_Phase_C | 51 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Current_Phase_Neut | 51 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Voltage_ A_N | 51 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Voltage_ B_N | 51 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_RMS_Voltage_ C_N | 51 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Active_Power_Phase_A | 51 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Active_Power_Phase_B | 51 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Active_Power_Phase_C | 51 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Total_Active_Power | 51 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Power_Factor_Phase_A | 51 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Power_Factor_Phase_B | 51 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Power_Factor_Phase_C | 51 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT135Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Power Distr. Panel Aft -10P1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT135Q01_Total_Power_Factor | 51 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Current_Phase_A | 52 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Current_Phase_B | 52 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Current_Phase_C | 52 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Current_Phase_Neut | 52 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Voltage_ A_N | 52 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Voltage_ B_N | 52 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_RMS_Voltage_ C_N | 52 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Active_Power_Phase_A | 52 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Active_Power_Phase_B | 52 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Active_Power_Phase_C | 52 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Total_Active_Power | 52 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Power_Factor_Phase_A | 52 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Power_Factor_Phase_B | 52 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Power_Factor_Phase_C | 52 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT136Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Dishwasher Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT136Q01_Total_Power_Factor | 52 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Current_Phase_A | 53 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Current_Phase_B | 53 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Current_Phase_C | 53 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Current_Phase_Neut | 53 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Voltage_ A_N | 53 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Voltage_ B_N | 53 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_RMS_Voltage_ C_N | 53 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Active_Power_Phase_A | 53 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Active_Power_Phase_B | 53 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Active_Power_Phase_C | 53 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Total_Active_Power | 53 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Power_Factor_Phase_A | 53 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Power_Factor_Phase_B | 53 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Power_Factor_Phase_C | 53 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT151Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Cooling Water Pump Main Propulsion Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT151Q01_Total_Power_Factor | 53 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Current_Phase_A | 54 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Current_Phase_B | 54 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Current_Phase_C | 54 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Current_Phase_Neut | 54 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Voltage_ A_N | 54 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Voltage_ B_N | 54 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_RMS_Voltage_ C_N | 54 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Active_Power_Phase_A | 54 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Active_Power_Phase_B | 54 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Active_Power_Phase_C | 54 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Total_Active_Power | 54 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Power_Factor_Phase_A | 54 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Power_Factor_Phase_B | 54 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Power_Factor_Phase_C | 54 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT155Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Compressor 1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT155Q01_Total_Power_Factor | 54 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Current_Phase_A | 55 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Current_Phase_B | 55 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Current_Phase_C | 55 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Current_Phase_Neut | 55 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Voltage_ A_N | 55 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Voltage_ B_N | 55 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_RMS_Voltage_ C_N | 55 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Active_Power_Phase_A | 55 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Active_Power_Phase_B | 55 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Active_Power_Phase_C | 55 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Total_Active_Power | 55 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Power_Factor_Phase_A | 55 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Power_Factor_Phase_B | 55 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Power_Factor_Phase_C | 55 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT156Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Heat Recovery Pump Compression Chiller Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT156Q01_Total_Power_Factor | 55 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Current_Phase_A | 56 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Current_Phase_B | 56 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Current_Phase_C | 56 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Current_Phase_Neut | 56 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Voltage_ A_N | 56 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Voltage_ B_N | 56 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_RMS_Voltage_ C_N | 56 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Active_Power_Phase_A | 56 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Active_Power_Phase_B | 56 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Active_Power_Phase_C | 56 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Total_Active_Power | 56 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Power_Factor_Phase_A | 56 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Power_Factor_Phase_B | 56 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Power_Factor_Phase_C | 56 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT157Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT157Q01_Total_Power_Factor | 56 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Current_Phase_A | 57 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Current_Phase_B | 57 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Current_Phase_C | 57 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Current_Phase_Neut | 57 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Voltage_ A_N | 57 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Voltage_ B_N | 57 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_RMS_Voltage_ C_N | 57 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Active_Power_Phase_A | 57 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Active_Power_Phase_B | 57 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Active_Power_Phase_C | 57 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Total_Active_Power | 57 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Power_Factor_Phase_A | 57 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Power_Factor_Phase_B | 57 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Power_Factor_Phase_C | 57 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT158Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Circulation Pump PVT Panles Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT158Q01_Total_Power_Factor | 57 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Current_Phase_A | 58 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Current_Phase_B | 58 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Current_Phase_C | 58 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Current_Phase_Neut | 58 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Voltage_ A_N | 58 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Voltage_ B_N | 58 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_RMS_Voltage_ C_N | 58 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Active_Power_Phase_A | 58 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Active_Power_Phase_B | 58 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Active_Power_Phase_C | 58 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Total_Active_Power | 58 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Power_Factor_Phase_A | 58 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Power_Factor_Phase_B | 58 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Power_Factor_Phase_C | 58 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT173Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT173Q01_Total_Power_Factor | 58 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Current_Phase_A | 59 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Current_Phase_B | 59 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Current_Phase_C | 59 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Current_Phase_Neut | 59 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Voltage_ A_N | 59 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Voltage_ B_N | 59 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_RMS_Voltage_ C_N | 59 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Active_Power_Phase_A | 59 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Active_Power_Phase_B | 59 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Active_Power_Phase_C | 59 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Total_Active_Power | 59 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Power_Factor_Phase_A | 59 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Power_Factor_Phase_B | 59 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Power_Factor_Phase_C | 59 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags1 |  |  |  |  | True | PT174Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.1 |  | Battery Room Ventilator PS Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.1 | $.PT174Q01_Total_Power_Factor | 59 | HoldingRegister | 3084 | [7 empty] | -
| True | [13 empty] | Serial Interface - AC Breakers +10P0.3 - AC DISTRIBUTION BOARD 400/230V PANEL 3
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Voltage_ A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Voltage_ B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_RMS_Voltage_ C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT320F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sewage Treatment Plant Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT320F01_Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Voltage_ A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Voltage_ B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_RMS_Voltage_ C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT329F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Propulsion Unit Offline Filter Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT329F01_Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Voltage_ A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Voltage_ B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_RMS_Voltage_ C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT330F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | AHU2000T Crew Mess Room Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT330F01_Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Voltage_ A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Voltage_ B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_RMS_Voltage_ C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT337F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fwd Main Propulsion Unit Ac Heating Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT337F01_Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Voltage_ A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Voltage_ B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_RMS_Voltage_ C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT338F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT338F01_Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Voltage_ A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Voltage_ B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_RMS_Voltage_ C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT339F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Submersible Bilge Pump 3 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT339F01_Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Voltage_ A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Voltage_ B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_RMS_Voltage_ C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT342F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT342F01_Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Voltage_ A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Voltage_ B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_RMS_Voltage_ C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT343F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT343F01_Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Voltage_ A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Voltage_ B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_RMS_Voltage_ C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT344F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT344F01_Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Voltage_ A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Voltage_ B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_RMS_Voltage_ C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT345F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Drain Tank Airco Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT345F01_Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Voltage_ A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Voltage_ B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_RMS_Voltage_ C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT346F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Watermaker Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT346F01_Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Voltage_ A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Voltage_ B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_RMS_Voltage_ C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT352F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Hydrophore 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT352F01_Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Voltage_ A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Voltage_ B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_RMS_Voltage_ C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT353F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chlorine Dosing Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT353F01_Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Voltage_ A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Voltage_ B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_RMS_Voltage_ C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT361F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Quooker Salon Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT361F01_Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Voltage_ A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Voltage_ B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_RMS_Voltage_ C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT362F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Main Salon Jb 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT362F01_Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Voltage_ A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Voltage_ B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_RMS_Voltage_ C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT363F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Serv. Corridor Jb Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT363F01_Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Voltage_ A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Voltage_ B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_RMS_Voltage_ C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT364F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Galley Drain Pump Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT364F01_Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Voltage_ A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Voltage_ B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_RMS_Voltage_ C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT365F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Helmstation PS/SB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT365F01_Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Voltage_ A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Voltage_ B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_RMS_Voltage_ C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT368F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 1) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT368F01_Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Voltage_ A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Voltage_ B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_RMS_Voltage_ C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT369F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Underwater Lights SB (Group 2) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT369F01_Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Voltage_ A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Voltage_ B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_RMS_Voltage_ C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT370F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Lighting Technical Space Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT370F01_Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Voltage_ A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Voltage_ B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_RMS_Voltage_ C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT371F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fan Coil Engine Office Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT371F01_Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Voltage_ A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Voltage_ B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_RMS_Voltage_ C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Sockets Main Technical Space Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376F01_Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Voltage_ A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Voltage_ B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_RMS_Voltage_ C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT377F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | ECDIS 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT377F01_Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Voltage_ A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Voltage_ B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_RMS_Voltage_ C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT378F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Captains Cabin Ships Office Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT378F01_Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Voltage_ A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Voltage_ B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_RMS_Voltage_ C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT379F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | KVM Mission Room Nav/Comm Locker Fwd Rack Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT379F01_Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Voltage_ A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Voltage_ B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_RMS_Voltage_ C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT380F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | EREC 2 Power Supply Heat Recovery Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT380F01_Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Voltage_ A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Voltage_ B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_RMS_Voltage_ C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT310Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT310Q01_Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Voltage_ A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Voltage_ B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_RMS_Voltage_ C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT311Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 3 Greywater Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT311Q01_Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Voltage_ A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Voltage_ B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_RMS_Voltage_ C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT312Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Dirty Oil Pump Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT312Q01_Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Voltage_ A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Voltage_ B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_RMS_Voltage_ C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT317Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Transfer Pump 2 Black Water Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT317Q01_Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Voltage_ A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Voltage_ B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_RMS_Voltage_ C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT331Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Technical Space Ventilator - Out Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT331Q01_Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Current_Phase_A | 33 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Current_Phase_B | 33 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Current_Phase_C | 33 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Current_Phase_Neut | 33 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Voltage_ A_N | 33 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Voltage_ B_N | 33 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_RMS_Voltage_ C_N | 33 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Active_Power_Phase_A | 33 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Active_Power_Phase_B | 33 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Active_Power_Phase_C | 33 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Total_Active_Power | 33 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Power_Factor_Phase_A | 33 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Power_Factor_Phase_B | 33 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Power_Factor_Phase_C | 33 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT333Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Fresh Air Unit Fore Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT333Q01_Total_Power_Factor | 33 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Current_Phase_A | 34 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Current_Phase_B | 34 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Current_Phase_C | 34 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Current_Phase_Neut | 34 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Voltage_ A_N | 34 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Voltage_ B_N | 34 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_RMS_Voltage_ C_N | 34 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Active_Power_Phase_A | 34 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Active_Power_Phase_B | 34 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Active_Power_Phase_C | 34 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Total_Active_Power | 34 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Power_Factor_Phase_A | 34 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Power_Factor_Phase_B | 34 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Power_Factor_Phase_C | 34 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT334Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Extraction Unit Fore Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT334Q01_Total_Power_Factor | 34 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Current_Phase_A | 35 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Current_Phase_B | 35 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Current_Phase_C | 35 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Current_Phase_Neut | 35 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Voltage_ A_N | 35 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Voltage_ B_N | 35 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_RMS_Voltage_ C_N | 35 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Active_Power_Phase_A | 35 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Active_Power_Phase_B | 35 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Active_Power_Phase_C | 35 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Total_Active_Power | 35 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Power_Factor_Phase_A | 35 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Power_Factor_Phase_B | 35 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Power_Factor_Phase_C | 35 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT335Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Power Distr. Panel Galley - 10P2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT335Q01_Total_Power_Factor | 35 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Current_Phase_A | 36 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Current_Phase_B | 36 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Current_Phase_C | 36 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Current_Phase_Neut | 36 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Voltage_ A_N | 36 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Voltage_ B_N | 36 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_RMS_Voltage_ C_N | 36 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Active_Power_Phase_A | 36 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Active_Power_Phase_B | 36 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Active_Power_Phase_C | 36 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Total_Active_Power | 36 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Power_Factor_Phase_A | 36 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Power_Factor_Phase_B | 36 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Power_Factor_Phase_C | 36 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT349Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Pressure Pump Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT349Q01_Total_Power_Factor | 36 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Current_Phase_A | 37 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Current_Phase_B | 37 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Current_Phase_C | 37 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Current_Phase_Neut | 37 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Voltage_ A_N | 37 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Voltage_ B_N | 37 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_RMS_Voltage_ C_N | 37 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Active_Power_Phase_A | 37 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Active_Power_Phase_B | 37 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Active_Power_Phase_C | 37 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Total_Active_Power | 37 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Power_Factor_Phase_A | 37 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Power_Factor_Phase_B | 37 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Power_Factor_Phase_C | 37 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT350Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Chilled Water Pump Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT350Q01_Total_Power_Factor | 37 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Current_Phase_A | 38 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Current_Phase_B | 38 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Current_Phase_C | 38 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Current_Phase_Neut | 38 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Voltage_ A_N | 38 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Voltage_ B_N | 38 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_RMS_Voltage_ C_N | 38 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Active_Power_Phase_A | 38 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Active_Power_Phase_B | 38 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Active_Power_Phase_C | 38 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Total_Active_Power | 38 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Power_Factor_Phase_A | 38 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Power_Factor_Phase_B | 38 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Power_Factor_Phase_C | 38 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT351Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Fwd Propulstion Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT351Q01_Total_Power_Factor | 38 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Current_Phase_A | 39 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Current_Phase_B | 39 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Current_Phase_C | 39 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Current_Phase_Neut | 39 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Voltage_ A_N | 39 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Voltage_ B_N | 39 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_RMS_Voltage_ C_N | 39 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Active_Power_Phase_A | 39 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Active_Power_Phase_B | 39 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Active_Power_Phase_C | 39 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Total_Active_Power | 39 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Power_Factor_Phase_A | 39 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Power_Factor_Phase_B | 39 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Power_Factor_Phase_C | 39 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT355Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Compressor 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT355Q01_Total_Power_Factor | 39 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Current_Phase_A | 40 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Current_Phase_B | 40 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Current_Phase_C | 40 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Current_Phase_Neut | 40 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Voltage_ A_N | 40 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Voltage_ B_N | 40 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_RMS_Voltage_ C_N | 40 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Active_Power_Phase_A | 40 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Active_Power_Phase_B | 40 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Active_Power_Phase_C | 40 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Total_Active_Power | 40 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Power_Factor_Phase_A | 40 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Power_Factor_Phase_B | 40 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Power_Factor_Phase_C | 40 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT356Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump Warm Water Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT356Q01_Total_Power_Factor | 40 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Current_Phase_A | 41 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Current_Phase_B | 41 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Current_Phase_C | 41 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Current_Phase_Neut | 41 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Voltage_ A_N | 41 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Voltage_ B_N | 41 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_RMS_Voltage_ C_N | 41 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Active_Power_Phase_A | 41 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Active_Power_Phase_B | 41 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Active_Power_Phase_C | 41 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Total_Active_Power | 41 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Power_Factor_Phase_A | 41 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Power_Factor_Phase_B | 41 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Power_Factor_Phase_C | 41 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT357Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Cooling Water Pump Adsorption Unit Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT357Q01_Total_Power_Factor | 41 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Current_Phase_A | 42 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Current_Phase_B | 42 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Current_Phase_C | 42 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Current_Phase_Neut | 42 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Voltage_ A_N | 42 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Voltage_ B_N | 42 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_RMS_Voltage_ C_N | 42 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Active_Power_Phase_A | 42 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Active_Power_Phase_B | 42 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Active_Power_Phase_C | 42 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Total_Active_Power | 42 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Power_Factor_Phase_A | 42 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Power_Factor_Phase_B | 42 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Power_Factor_Phase_C | 42 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT358Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circulation Pump PVT Panels Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT358Q01_Total_Power_Factor | 42 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Current_Phase_A | 43 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Current_Phase_B | 43 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Current_Phase_C | 43 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Current_Phase_Neut | 43 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Voltage_ A_N | 43 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Voltage_ B_N | 43 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_RMS_Voltage_ C_N | 43 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Active_Power_Phase_A | 43 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Active_Power_Phase_B | 43 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Active_Power_Phase_C | 43 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Total_Active_Power | 43 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Power_Factor_Phase_A | 43 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Power_Factor_Phase_B | 43 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Power_Factor_Phase_C | 43 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT359Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Heat. Water Fresh Hotwater System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT359Q01_Total_Power_Factor | 43 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Current_Phase_A | 44 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Current_Phase_B | 44 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Current_Phase_C | 44 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Current_Phase_Neut | 44 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Voltage_ A_N | 44 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Voltage_ B_N | 44 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_RMS_Voltage_ C_N | 44 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Active_Power_Phase_A | 44 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Active_Power_Phase_B | 44 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Active_Power_Phase_C | 44 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Total_Active_Power | 44 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Power_Factor_Phase_A | 44 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Power_Factor_Phase_B | 44 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Power_Factor_Phase_C | 44 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT360Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Circ. Pump Cooling Water Electrical System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT360Q01_Total_Power_Factor | 44 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Current_Phase_A | 45 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Current_Phase_B | 45 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Current_Phase_C | 45 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Current_Phase_Neut | 45 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Voltage_ A_N | 45 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Voltage_ B_N | 45 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_RMS_Voltage_ C_N | 45 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Active_Power_Phase_A | 45 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Active_Power_Phase_B | 45 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Active_Power_Phase_C | 45 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Total_Active_Power | 45 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Power_Factor_Phase_A | 45 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Power_Factor_Phase_B | 45 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Power_Factor_Phase_C | 45 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT374Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT374Q01_Total_Power_Factor | 45 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Current_Phase_A | 46 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Current_Phase_B | 46 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Current_Phase_C | 46 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Current_Phase_Neut | 46 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Voltage_ A_N | 46 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Voltage_ B_N | 46 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_RMS_Voltage_ C_N | 46 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Active_Power_Phase_A | 46 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Active_Power_Phase_B | 46 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Active_Power_Phase_C | 46 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Total_Active_Power | 46 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Power_Factor_Phase_A | 46 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Power_Factor_Phase_B | 46 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Power_Factor_Phase_C | 46 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT375Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Battery Room Ventilator SB Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT375Q01_Total_Power_Factor | 46 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Current_Phase_A | 47 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Current_Phase_B | 47 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Current_Phase_C | 47 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Current_Phase_Neut | 47 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Voltage_ A_N | 47 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Voltage_ B_N | 47 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_RMS_Voltage_ C_N | 47 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Active_Power_Phase_A | 47 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Active_Power_Phase_B | 47 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Active_Power_Phase_C | 47 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Total_Active_Power | 47 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Power_Factor_Phase_A | 47 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Power_Factor_Phase_B | 47 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Power_Factor_Phase_C | 47 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags2 |  |  |  |  | True | PT376Q01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P0.3 |  | Welding Socket Lazarette Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P0.3 | $.PT376Q01_Total_Power_Factor | 47 | HoldingRegister | 3084 | [7 empty] | -
| True | [13 empty] | Serial Interface - AC Breakers +10P1 - AC DISTRIBUTION BOARD 400/230V AFT GUEST CORRIDOR
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Voltage_ A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Voltage_ B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_RMS_Voltage_ C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT10F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT10F01_Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Voltage_ A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Voltage_ B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_RMS_Voltage_ C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT11F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT11F01_Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Voltage_ A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Voltage_ B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_RMS_Voltage_ C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT12F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT12F01_Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Voltage_ A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Voltage_ B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_RMS_Voltage_ C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT19F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Aft Peak Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT19F01_Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Voltage_ A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Voltage_ B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_RMS_Voltage_ C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT20F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Ventilator Bilge Aft Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT20F01_Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Voltage_ A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Voltage_ B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_RMS_Voltage_ C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT21F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Deck Lounge Guest Cabin Aft SB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT21F01_Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Voltage_ A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Voltage_ B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_RMS_Voltage_ C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT22F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Technical Space Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT22F01_Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Voltage_ A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Voltage_ B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_RMS_Voltage_ C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT23F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Guest Cabin Fwd PS Guest Cabin Aft PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT23F01_Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Voltage_ A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Voltage_ B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_RMS_Voltage_ C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT24F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(Hers) Owners State Room PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT24F01_Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Voltage_ A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Voltage_ B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_RMS_Voltage_ C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT25F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Bath.(His) Owners State Room SB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT25F01_Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Voltage_ A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Voltage_ B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_RMS_Voltage_ C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT26F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Ships Office Watersport Storage Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT26F01_Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Voltage_ A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Voltage_ B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_RMS_Voltage_ C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT27F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | FCU: Owners Deckh. Dining Main Salon Lounge Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT27F01_Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Voltage_ A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Voltage_ B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_RMS_Voltage_ C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT28F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AHU1500 Aft Area Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT28F01_Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Voltage_ A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Voltage_ B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_RMS_Voltage_ C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT29F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Discharge Pump Mast Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT29F01_Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Voltage_ A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Voltage_ B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_RMS_Voltage_ C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT30F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Lights Technical Area Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT30F01_Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Voltage_ A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Voltage_ B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_RMS_Voltage_ C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT31F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT31F01_Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Voltage_ A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Voltage_ B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_RMS_Voltage_ C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT32F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 3 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT32F01_Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Voltage_ A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Voltage_ B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_RMS_Voltage_ C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT33F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP125 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT33F01_Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Voltage_ A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Voltage_ B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_RMS_Voltage_ C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT34F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner - EMP126 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT34F01_Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Voltage_ A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Voltage_ B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_RMS_Voltage_ C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT35F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Guest Cabin 4 - EMP124 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT35F01_Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Voltage_ A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Voltage_ B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_RMS_Voltage_ C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT36F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Lower Deck Lounge - EMP121 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT36F01_Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Voltage_ A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Voltage_ B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_RMS_Voltage_ C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT37F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Outlets Owner Private Lounge - EMP220 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT37F01_Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Voltage_ A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Voltage_ B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_RMS_Voltage_ C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT38F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | KNX Supply - EMP121 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT38F01_Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Voltage_ A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Voltage_ B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_RMS_Voltage_ C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT39F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT39F01_Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Voltage_ A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Voltage_ B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_RMS_Voltage_ C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT40F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT40F01_Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Voltage_ A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Voltage_ B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_RMS_Voltage_ C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT41F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT41F01_Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Voltage_ A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Voltage_ B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_RMS_Voltage_ C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT60F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Starlink Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT60F01_Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Voltage_ A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Voltage_ B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_RMS_Voltage_ C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT61F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Diving Compressor Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT61F01_Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Voltage_ A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Voltage_ B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_RMS_Voltage_ C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT62F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Burglar Alarm System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT62F01_Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Voltage_ A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Voltage_ B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_RMS_Voltage_ C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT63F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | AV System Supply #1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT63F01_Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Voltage_ A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Voltage_ B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_RMS_Voltage_ C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT64F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Sliding Window Private Salon Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT64F01_Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Current_Phase_Neut | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Voltage_ A_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Voltage_ A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Voltage_ B_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Voltage_ B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_RMS_Voltage_ C_N | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_RMS_Voltage_ C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Active_Power_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Active_Power_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Active_Power_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Total_Active_Power | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Power_Factor_Phase_A | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Power_Factor_Phase_B | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Power_Factor_Phase_C | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags3 |  |  |  |  | True | PT107F01_Total_Power_Factor | +CB.1 |  | 1000 | AC DISTR +10P1 |  | Supply Greenwall Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P1 | $.PT107F01_Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
| True | [13 empty] | Serial Interface - AC Breakers +10P2 - AC DISTRIBUTION BOARD 400/230V GALLEY
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Voltage_ A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Voltage_ B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_RMS_Voltage_ C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT10F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Induction Cooktop Galley Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT10F01_Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Voltage_ A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Voltage_ B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_RMS_Voltage_ C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT11F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT11F01_Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Voltage_ A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Voltage_ B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_RMS_Voltage_ C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT12F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Dishwasher Galley-2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT12F01_Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Voltage_ A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Voltage_ B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_RMS_Voltage_ C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT13F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Oven Galley Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT13F01_Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Voltage_ A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Voltage_ B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_RMS_Voltage_ C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT14F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Steam Oven Galley Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT14F01_Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Voltage_ A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Voltage_ B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_RMS_Voltage_ C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT15F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Service Sink Galley Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT15F01_Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Voltage_ A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Voltage_ B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_RMS_Voltage_ C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT16F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Quooker Chef Sink Galley Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT16F01_Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Voltage_ A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Voltage_ B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_RMS_Voltage_ C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT17F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT17F01_Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Voltage_ A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Voltage_ B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_RMS_Voltage_ C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT18F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley JB-2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT18F01_Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Voltage_ A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Voltage_ B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_RMS_Voltage_ C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT19F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Walk In Freezer Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT19F01_Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Voltage_ A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Voltage_ B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_RMS_Voltage_ C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT20F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Fridge Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT20F01_Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Voltage_ A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Voltage_ B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_RMS_Voltage_ C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT21F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Fridge System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT21F01_Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Voltage_ A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Voltage_ B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_RMS_Voltage_ C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT22F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Compressor Freeze System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT22F01_Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Voltage_ A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Voltage_ B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_RMS_Voltage_ C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT23F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Discharge Pump Galley/Crew Mess Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT23F01_Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Voltage_ A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Voltage_ B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_RMS_Voltage_ C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT24F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT24F01_Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Voltage_ A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Voltage_ B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_RMS_Voltage_ C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT25F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Socket Circuit 3 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT25F01_Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Voltage_ A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Voltage_ B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_RMS_Voltage_ C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT26F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Fridge System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT26F01_Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Voltage_ A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Voltage_ B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_RMS_Voltage_ C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT27F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Evaporator Freeze System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT27F01_Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Voltage_ A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Voltage_ B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_RMS_Voltage_ C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT40F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Circulation Pump Cooling Set Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT40F01_Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Voltage_ A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Voltage_ B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_RMS_Voltage_ C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT41F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Drain Pump Galley Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT41F01_Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Voltage_ A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Voltage_ B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_RMS_Voltage_ C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F01_Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Voltage_ A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Voltage_ B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_RMS_Voltage_ C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT50F02_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | FCU: Galley Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT50F02_Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Voltage_ A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Voltage_ B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_RMS_Voltage_ C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT53F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Galley Hood Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT53F01_Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Voltage_ A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Voltage_ B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_RMS_Voltage_ C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT60F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT60F01_Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Voltage_ A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Voltage_ B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_RMS_Voltage_ C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags4 |  |  |  |  | True | PT61F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P2 |  | Outlets Galley - EMP 111 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P2 | $.PT61F01_Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
| True | [13 empty] | Serial Interface - AC Breakers +10P3 - AC DISTRIBUTION BOARD 400/230V FWD GUEST CORRIDOR
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Current_Phase_A | 1 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Current_Phase_B | 1 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Current_Phase_C | 1 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Current_Phase_Neut | 1 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Voltage_ A_N | 1 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Voltage_ B_N | 1 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_RMS_Voltage_ C_N | 1 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Active_Power_Phase_A | 1 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Active_Power_Phase_B | 1 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Active_Power_Phase_C | 1 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Total_Active_Power | 1 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Power_Factor_Phase_A | 1 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Power_Factor_Phase_B | 1 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Power_Factor_Phase_C | 1 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT10F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-1 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT10F01_Total_Power_Factor | 1 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Current_Phase_A | 2 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Current_Phase_B | 2 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Current_Phase_C | 2 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Current_Phase_Neut | 2 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Voltage_ A_N | 2 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Voltage_ B_N | 2 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_RMS_Voltage_ C_N | 2 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Active_Power_Phase_A | 2 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Active_Power_Phase_B | 2 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Active_Power_Phase_C | 2 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Total_Active_Power | 2 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Power_Factor_Phase_A | 2 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Power_Factor_Phase_B | 2 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Power_Factor_Phase_C | 2 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT11F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Washer-2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT11F01_Total_Power_Factor | 2 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Current_Phase_A | 3 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Current_Phase_B | 3 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Current_Phase_C | 3 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Current_Phase_Neut | 3 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Voltage_ A_N | 3 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Voltage_ B_N | 3 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_RMS_Voltage_ C_N | 3 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Active_Power_Phase_A | 3 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Active_Power_Phase_B | 3 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Active_Power_Phase_C | 3 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Total_Active_Power | 3 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Power_Factor_Phase_A | 3 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Power_Factor_Phase_B | 3 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Power_Factor_Phase_C | 3 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT12F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dishwasher Crew Mess Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT12F01_Total_Power_Factor | 3 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Current_Phase_A | 4 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Current_Phase_B | 4 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Current_Phase_C | 4 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Current_Phase_Neut | 4 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Voltage_ A_N | 4 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Voltage_ B_N | 4 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_RMS_Voltage_ C_N | 4 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Active_Power_Phase_A | 4 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Active_Power_Phase_B | 4 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Active_Power_Phase_C | 4 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Total_Active_Power | 4 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Power_Factor_Phase_A | 4 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Power_Factor_Phase_B | 4 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Power_Factor_Phase_C | 4 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT13F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Dryer-1 and Dryer-2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT13F01_Total_Power_Factor | 4 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Current_Phase_A | 5 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Current_Phase_B | 5 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Current_Phase_C | 5 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Current_Phase_Neut | 5 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Voltage_ A_N | 5 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Voltage_ B_N | 5 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_RMS_Voltage_ C_N | 5 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Active_Power_Phase_A | 5 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Active_Power_Phase_B | 5 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Active_Power_Phase_C | 5 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Total_Active_Power | 5 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Power_Factor_Phase_A | 5 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Power_Factor_Phase_B | 5 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Power_Factor_Phase_C | 5 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT14F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT14F01_Total_Power_Factor | 5 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Current_Phase_A | 6 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Current_Phase_B | 6 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Current_Phase_C | 6 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Current_Phase_Neut | 6 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Voltage_ A_N | 6 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Voltage_ B_N | 6 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_RMS_Voltage_ C_N | 6 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Active_Power_Phase_A | 6 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Active_Power_Phase_B | 6 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Active_Power_Phase_C | 6 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Total_Active_Power | 6 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Power_Factor_Phase_A | 6 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Power_Factor_Phase_B | 6 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Power_Factor_Phase_C | 6 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT15F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sockets Crew Cabins SB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT15F01_Total_Power_Factor | 6 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Current_Phase_A | 7 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Current_Phase_B | 7 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Current_Phase_C | 7 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Current_Phase_Neut | 7 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Voltage_ A_N | 7 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Voltage_ B_N | 7 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_RMS_Voltage_ C_N | 7 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Active_Power_Phase_A | 7 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Active_Power_Phase_B | 7 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Active_Power_Phase_C | 7 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Total_Active_Power | 7 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Power_Factor_Phase_A | 7 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Power_Factor_Phase_B | 7 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Power_Factor_Phase_C | 7 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT16F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | MFHF SSB (Main Supply) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT16F01_Total_Power_Factor | 7 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Current_Phase_A | 8 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Current_Phase_B | 8 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Current_Phase_C | 8 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Current_Phase_Neut | 8 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Voltage_ A_N | 8 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Voltage_ B_N | 8 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_RMS_Voltage_ C_N | 8 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Active_Power_Phase_A | 8 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Active_Power_Phase_B | 8 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Active_Power_Phase_C | 8 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Total_Active_Power | 8 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Power_Factor_Phase_A | 8 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Power_Factor_Phase_B | 8 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Power_Factor_Phase_C | 8 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT17F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Sliding Door Crew Corridor Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT17F01_Total_Power_Factor | 8 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Current_Phase_A | 9 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Current_Phase_B | 9 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Current_Phase_C | 9 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Current_Phase_Neut | 9 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Voltage_ A_N | 9 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Voltage_ B_N | 9 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_RMS_Voltage_ C_N | 9 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Active_Power_Phase_A | 9 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Active_Power_Phase_B | 9 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Active_Power_Phase_C | 9 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Total_Active_Power | 9 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Power_Factor_Phase_A | 9 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Power_Factor_Phase_B | 9 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Power_Factor_Phase_C | 9 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT18F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Crew Mess JB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT18F01_Total_Power_Factor | 9 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Current_Phase_A | 10 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Current_Phase_B | 10 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Current_Phase_C | 10 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Current_Phase_Neut | 10 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Voltage_ A_N | 10 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Voltage_ B_N | 10 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_RMS_Voltage_ C_N | 10 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Active_Power_Phase_A | 10 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Active_Power_Phase_B | 10 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Active_Power_Phase_C | 10 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Total_Active_Power | 10 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Power_Factor_Phase_A | 10 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Power_Factor_Phase_B | 10 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Power_Factor_Phase_C | 10 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT19F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT19F01_Total_Power_Factor | 10 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Current_Phase_A | 11 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Current_Phase_B | 11 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Current_Phase_C | 11 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Current_Phase_Neut | 11 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Voltage_ A_N | 11 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Voltage_ B_N | 11 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_RMS_Voltage_ C_N | 11 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Active_Power_Phase_A | 11 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Active_Power_Phase_B | 11 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Active_Power_Phase_C | 11 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Total_Active_Power | 11 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Power_Factor_Phase_A | 11 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Power_Factor_Phase_B | 11 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Power_Factor_Phase_C | 11 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT20F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Interiour Siding Door Galley Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT20F01_Total_Power_Factor | 11 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Current_Phase_A | 12 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Current_Phase_B | 12 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Current_Phase_C | 12 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Current_Phase_Neut | 12 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Voltage_ A_N | 12 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Voltage_ B_N | 12 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_RMS_Voltage_ C_N | 12 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Active_Power_Phase_A | 12 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Active_Power_Phase_B | 12 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Active_Power_Phase_C | 12 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Total_Active_Power | 12 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Power_Factor_Phase_A | 12 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Power_Factor_Phase_B | 12 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Power_Factor_Phase_C | 12 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT21F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Main Companion Way Door System Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT21F01_Total_Power_Factor | 12 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Current_Phase_A | 13 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Current_Phase_B | 13 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Current_Phase_C | 13 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Current_Phase_Neut | 13 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Voltage_ A_N | 13 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Voltage_ B_N | 13 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_RMS_Voltage_ C_N | 13 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Active_Power_Phase_A | 13 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Active_Power_Phase_B | 13 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Active_Power_Phase_C | 13 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Total_Active_Power | 13 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Power_Factor_Phase_A | 13 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Power_Factor_Phase_B | 13 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Power_Factor_Phase_C | 13 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT22F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Entrance Door Aft Deckhouse Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT22F01_Total_Power_Factor | 13 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Current_Phase_A | 14 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Current_Phase_B | 14 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Current_Phase_C | 14 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Current_Phase_Neut | 14 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Voltage_ A_N | 14 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Voltage_ B_N | 14 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_RMS_Voltage_ C_N | 14 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Active_Power_Phase_A | 14 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Active_Power_Phase_B | 14 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Active_Power_Phase_C | 14 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Total_Active_Power | 14 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Power_Factor_Phase_A | 14 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Power_Factor_Phase_B | 14 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Power_Factor_Phase_C | 14 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT23F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Door Crew Entrance Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT23F01_Total_Power_Factor | 14 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Current_Phase_A | 15 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Current_Phase_B | 15 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Current_Phase_C | 15 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Current_Phase_Neut | 15 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Voltage_ A_N | 15 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Voltage_ B_N | 15 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_RMS_Voltage_ C_N | 15 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Active_Power_Phase_A | 15 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Active_Power_Phase_B | 15 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Active_Power_Phase_C | 15 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Total_Active_Power | 15 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Power_Factor_Phase_A | 15 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Power_Factor_Phase_B | 15 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Power_Factor_Phase_C | 15 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT24F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew SB Aft/Mid Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT24F01_Total_Power_Factor | 15 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Current_Phase_A | 16 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Current_Phase_B | 16 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Current_Phase_C | 16 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Current_Phase_Neut | 16 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Voltage_ A_N | 16 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Voltage_ B_N | 16 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_RMS_Voltage_ C_N | 16 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Active_Power_Phase_A | 16 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Active_Power_Phase_B | 16 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Active_Power_Phase_C | 16 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Total_Active_Power | 16 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Power_Factor_Phase_A | 16 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Power_Factor_Phase_B | 16 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Power_Factor_Phase_C | 16 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT25F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Crew PS Mid/Sb Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT25F01_Total_Power_Factor | 16 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Current_Phase_A | 17 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Current_Phase_B | 17 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Current_Phase_C | 17 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Current_Phase_Neut | 17 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Voltage_ A_N | 17 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Voltage_ B_N | 17 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_RMS_Voltage_ C_N | 17 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Active_Power_Phase_A | 17 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Active_Power_Phase_B | 17 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Active_Power_Phase_C | 17 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Total_Active_Power | 17 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Power_Factor_Phase_A | 17 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Power_Factor_Phase_B | 17 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Power_Factor_Phase_C | 17 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT26F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT26F01_Total_Power_Factor | 17 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Current_Phase_A | 18 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Current_Phase_B | 18 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Current_Phase_C | 18 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Current_Phase_Neut | 18 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Voltage_ A_N | 18 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Voltage_ B_N | 18 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_RMS_Voltage_ C_N | 18 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Active_Power_Phase_A | 18 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Active_Power_Phase_B | 18 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Active_Power_Phase_C | 18 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Total_Active_Power | 18 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Power_Factor_Phase_A | 18 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Power_Factor_Phase_B | 18 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Power_Factor_Phase_C | 18 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT27F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Circulation Pump Wall & Ceiling Cooling Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT27F01_Total_Power_Factor | 18 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Current_Phase_A | 19 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Current_Phase_B | 19 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Current_Phase_C | 19 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Current_Phase_Neut | 19 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Voltage_ A_N | 19 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Voltage_ B_N | 19 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_RMS_Voltage_ C_N | 19 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Active_Power_Phase_A | 19 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Active_Power_Phase_B | 19 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Active_Power_Phase_C | 19 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Total_Active_Power | 19 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Power_Factor_Phase_A | 19 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Power_Factor_Phase_B | 19 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Power_Factor_Phase_C | 19 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT28F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT28F01_Total_Power_Factor | 19 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Current_Phase_A | 20 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Current_Phase_B | 20 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Current_Phase_C | 20 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Current_Phase_Neut | 20 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Voltage_ A_N | 20 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Voltage_ B_N | 20 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_RMS_Voltage_ C_N | 20 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Active_Power_Phase_A | 20 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Active_Power_Phase_B | 20 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Active_Power_Phase_C | 20 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Total_Active_Power | 20 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Power_Factor_Phase_A | 20 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Power_Factor_Phase_B | 20 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Power_Factor_Phase_C | 20 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT29F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 4 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT29F01_Total_Power_Factor | 20 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Current_Phase_A | 21 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Current_Phase_B | 21 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Current_Phase_C | 21 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Current_Phase_Neut | 21 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Voltage_ A_N | 21 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Voltage_ B_N | 21 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_RMS_Voltage_ C_N | 21 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Active_Power_Phase_A | 21 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Active_Power_Phase_B | 21 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Active_Power_Phase_C | 21 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Total_Active_Power | 21 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Power_Factor_Phase_A | 21 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Power_Factor_Phase_B | 21 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Power_Factor_Phase_C | 21 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT30F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Wall & Ceiling Cooling Pump Section 5 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT30F01_Total_Power_Factor | 21 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Current_Phase_A | 22 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Current_Phase_B | 22 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Current_Phase_C | 22 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Current_Phase_Neut | 22 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Voltage_ A_N | 22 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Voltage_ B_N | 22 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_RMS_Voltage_ C_N | 22 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Active_Power_Phase_A | 22 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Active_Power_Phase_B | 22 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Active_Power_Phase_C | 22 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Total_Active_Power | 22 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Power_Factor_Phase_A | 22 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Power_Factor_Phase_B | 22 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Power_Factor_Phase_C | 22 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT31F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Guest Cabin PS Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT31F01_Total_Power_Factor | 22 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Current_Phase_A | 23 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Current_Phase_B | 23 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Current_Phase_C | 23 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Current_Phase_Neut | 23 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Voltage_ A_N | 23 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Voltage_ B_N | 23 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_RMS_Voltage_ C_N | 23 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Active_Power_Phase_A | 23 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Active_Power_Phase_B | 23 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Active_Power_Phase_C | 23 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Total_Active_Power | 23 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Power_Factor_Phase_A | 23 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Power_Factor_Phase_B | 23 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Power_Factor_Phase_C | 23 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT32F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | To Overflow Cabin Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT32F01_Total_Power_Factor | 23 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Current_Phase_A | 24 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Current_Phase_B | 24 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Current_Phase_C | 24 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Current_Phase_Neut | 24 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Voltage_ A_N | 24 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Voltage_ B_N | 24 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_RMS_Voltage_ C_N | 24 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Active_Power_Phase_A | 24 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Active_Power_Phase_B | 24 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Active_Power_Phase_C | 24 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Total_Active_Power | 24 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Power_Factor_Phase_A | 24 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Power_Factor_Phase_B | 24 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Power_Factor_Phase_C | 24 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT33F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Captains Cabin Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT33F01_Total_Power_Factor | 24 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Current_Phase_A | 25 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Current_Phase_B | 25 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Current_Phase_C | 25 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Current_Phase_Neut | 25 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Voltage_ A_N | 25 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Voltage_ B_N | 25 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_RMS_Voltage_ C_N | 25 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Active_Power_Phase_A | 25 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Active_Power_Phase_B | 25 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Active_Power_Phase_C | 25 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Total_Active_Power | 25 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Power_Factor_Phase_A | 25 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Power_Factor_Phase_B | 25 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Power_Factor_Phase_C | 25 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT34F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Aft Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT34F01_Total_Power_Factor | 25 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Current_Phase_A | 26 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Current_Phase_B | 26 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Current_Phase_C | 26 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Current_Phase_Neut | 26 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Voltage_ A_N | 26 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Voltage_ B_N | 26 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_RMS_Voltage_ C_N | 26 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Active_Power_Phase_A | 26 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Active_Power_Phase_B | 26 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Active_Power_Phase_C | 26 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Total_Active_Power | 26 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Power_Factor_Phase_A | 26 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Power_Factor_Phase_B | 26 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Power_Factor_Phase_C | 26 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT35F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Mid Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT35F01_Total_Power_Factor | 26 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Current_Phase_A | 27 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Current_Phase_B | 27 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Current_Phase_C | 27 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Current_Phase_Neut | 27 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Voltage_ A_N | 27 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Voltage_ B_N | 27 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_RMS_Voltage_ C_N | 27 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Active_Power_Phase_A | 27 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Active_Power_Phase_B | 27 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Active_Power_Phase_C | 27 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Total_Active_Power | 27 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Power_Factor_Phase_A | 27 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Power_Factor_Phase_B | 27 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Power_Factor_Phase_C | 27 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT36F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Mid Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT36F01_Total_Power_Factor | 27 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Current_Phase_A | 28 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Current_Phase_B | 28 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Current_Phase_C | 28 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Current_Phase_Neut | 28 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Voltage_ A_N | 28 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Voltage_ B_N | 28 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_RMS_Voltage_ C_N | 28 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Active_Power_Phase_A | 28 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Active_Power_Phase_B | 28 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Active_Power_Phase_C | 28 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Total_Active_Power | 28 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Power_Factor_Phase_A | 28 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Power_Factor_Phase_B | 28 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Power_Factor_Phase_C | 28 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT37F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin SB Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT37F01_Total_Power_Factor | 28 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Current_Phase_A | 29 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Current_Phase_B | 29 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Current_Phase_C | 29 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Current_Phase_Neut | 29 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Voltage_ A_N | 29 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Voltage_ B_N | 29 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_RMS_Voltage_ C_N | 29 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Active_Power_Phase_A | 29 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Active_Power_Phase_B | 29 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Active_Power_Phase_C | 29 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Total_Active_Power | 29 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Power_Factor_Phase_A | 29 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Power_Factor_Phase_B | 29 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Power_Factor_Phase_C | 29 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT38F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Toilet Crew Cabin PS Fwd Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT38F01_Total_Power_Factor | 29 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Current_Phase_A | 30 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Current_Phase_B | 30 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Current_Phase_C | 30 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Current_Phase_Neut | 30 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Voltage_ A_N | 30 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Voltage_ B_N | 30 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_RMS_Voltage_ C_N | 30 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Active_Power_Phase_A | 30 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Active_Power_Phase_B | 30 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Active_Power_Phase_C | 30 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Total_Active_Power | 30 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Power_Factor_Phase_A | 30 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Power_Factor_Phase_B | 30 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Power_Factor_Phase_C | 30 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT39F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Aft Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT39F01_Total_Power_Factor | 30 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Current_Phase_A | 31 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Current_Phase_B | 31 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Current_Phase_C | 31 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Current_Phase_Neut | 31 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Voltage_ A_N | 31 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Voltage_ B_N | 31 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_RMS_Voltage_ C_N | 31 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Active_Power_Phase_A | 31 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Active_Power_Phase_B | 31 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Active_Power_Phase_C | 31 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Total_Active_Power | 31 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Power_Factor_Phase_A | 31 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Power_Factor_Phase_B | 31 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Power_Factor_Phase_C | 31 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT40F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 5) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT40F01_Total_Power_Factor | 31 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Current_Phase_A | 32 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Current_Phase_B | 32 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Current_Phase_C | 32 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Current_Phase_Neut | 32 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Voltage_ A_N | 32 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Voltage_ B_N | 32 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_RMS_Voltage_ C_N | 32 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Active_Power_Phase_A | 32 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Active_Power_Phase_B | 32 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Active_Power_Phase_C | 32 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Total_Active_Power | 32 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Power_Factor_Phase_A | 32 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Power_Factor_Phase_B | 32 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Power_Factor_Phase_C | 32 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT41F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lighting Fore Ship (Section 4) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT41F01_Total_Power_Factor | 32 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Current_Phase_A | 33 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Current_Phase_B | 33 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Current_Phase_C | 33 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Current_Phase_Neut | 33 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Voltage_ A_N | 33 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Voltage_ B_N | 33 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_RMS_Voltage_ C_N | 33 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Active_Power_Phase_A | 33 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Active_Power_Phase_B | 33 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Active_Power_Phase_C | 33 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Total_Active_Power | 33 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Power_Factor_Phase_A | 33 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Power_Factor_Phase_B | 33 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Power_Factor_Phase_C | 33 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT42F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare (Lighting) Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT42F01_Total_Power_Factor | 33 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Current_Phase_A | 34 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Current_Phase_B | 34 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Current_Phase_C | 34 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Current_Phase_Neut | 34 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Voltage_ A_N | 34 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Voltage_ B_N | 34 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_RMS_Voltage_ C_N | 34 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Active_Power_Phase_A | 34 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Active_Power_Phase_B | 34 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Active_Power_Phase_C | 34 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Total_Active_Power | 34 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Power_Factor_Phase_A | 34 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Power_Factor_Phase_B | 34 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Power_Factor_Phase_C | 34 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT51F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Fore Peak Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT51F01_Total_Power_Factor | 34 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Current_Phase_A | 35 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Current_Phase_B | 35 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Current_Phase_C | 35 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Current_Phase_Neut | 35 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Voltage_ A_N | 35 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Voltage_ B_N | 35 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_RMS_Voltage_ C_N | 35 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Active_Power_Phase_A | 35 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Active_Power_Phase_B | 35 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Active_Power_Phase_C | 35 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Total_Active_Power | 35 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Power_Factor_Phase_A | 35 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Power_Factor_Phase_B | 35 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Power_Factor_Phase_C | 35 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT52F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Ventilator Bilge Fore Ship Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT52F01_Total_Power_Factor | 35 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Current_Phase_A | 36 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Current_Phase_B | 36 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Current_Phase_C | 36 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Current_Phase_Neut | 36 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Voltage_ A_N | 36 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Voltage_ B_N | 36 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_RMS_Voltage_ C_N | 36 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Active_Power_Phase_A | 36 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Active_Power_Phase_B | 36 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Active_Power_Phase_C | 36 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Total_Active_Power | 36 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Power_Factor_Phase_A | 36 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Power_Factor_Phase_B | 36 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Power_Factor_Phase_C | 36 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT53F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Guest Fwd Cabin PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT53F01_Total_Power_Factor | 36 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Current_Phase_A | 37 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Current_Phase_B | 37 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Current_Phase_C | 37 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Current_Phase_Neut | 37 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Voltage_ A_N | 37 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Voltage_ B_N | 37 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_RMS_Voltage_ C_N | 37 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Active_Power_Phase_A | 37 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Active_Power_Phase_B | 37 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Active_Power_Phase_C | 37 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Total_Active_Power | 37 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Power_Factor_Phase_A | 37 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Power_Factor_Phase_B | 37 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Power_Factor_Phase_C | 37 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT54F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU Overflow Bathroom Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT54F01_Total_Power_Factor | 37 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Current_Phase_A | 38 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Current_Phase_B | 38 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Current_Phase_C | 38 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Current_Phase_Neut | 38 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Voltage_ A_N | 38 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Voltage_ B_N | 38 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_RMS_Voltage_ C_N | 38 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Active_Power_Phase_A | 38 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Active_Power_Phase_B | 38 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Active_Power_Phase_C | 38 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Total_Active_Power | 38 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Power_Factor_Phase_A | 38 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Power_Factor_Phase_B | 38 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Power_Factor_Phase_C | 38 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT55F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Laundry Captain Cabin Crew Cabin Mid PS Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT55F01_Total_Power_Factor | 38 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Current_Phase_A | 39 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Current_Phase_B | 39 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Current_Phase_C | 39 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Current_Phase_Neut | 39 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Voltage_ A_N | 39 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Voltage_ B_N | 39 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_RMS_Voltage_ C_N | 39 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Active_Power_Phase_A | 39 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Active_Power_Phase_B | 39 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Active_Power_Phase_C | 39 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Total_Active_Power | 39 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Power_Factor_Phase_A | 39 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Power_Factor_Phase_B | 39 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Power_Factor_Phase_C | 39 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT56F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Mess Crew Cabin Aft Sb Crew Cabin Mid SB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT56F01_Total_Power_Factor | 39 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Current_Phase_A | 40 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Current_Phase_B | 40 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Current_Phase_C | 40 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Current_Phase_Neut | 40 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Voltage_ A_N | 40 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Voltage_ B_N | 40 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_RMS_Voltage_ C_N | 40 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Active_Power_Phase_A | 40 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Active_Power_Phase_B | 40 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Active_Power_Phase_C | 40 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Total_Active_Power | 40 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Power_Factor_Phase_A | 40 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Power_Factor_Phase_B | 40 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Power_Factor_Phase_C | 40 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT57F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Crew Cabin Fwd Ps Crew Cabin Fwd SB Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT57F01_Total_Power_Factor | 40 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Current_Phase_A | 41 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Current_Phase_B | 41 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Current_Phase_C | 41 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Current_Phase_Neut | 41 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Voltage_ A_N | 41 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Voltage_ B_N | 41 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_RMS_Voltage_ C_N | 41 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Active_Power_Phase_A | 41 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Active_Power_Phase_B | 41 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Active_Power_Phase_C | 41 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Total_Active_Power | 41 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Power_Factor_Phase_A | 41 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Power_Factor_Phase_B | 41 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Power_Factor_Phase_C | 41 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT58F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | FCU: Main Salon Bar Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT58F01_Total_Power_Factor | 41 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Current_Phase_A | 42 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Current_Phase_B | 42 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Current_Phase_C | 42 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Current_Phase_Neut | 42 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Voltage_ A_N | 42 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Voltage_ B_N | 42 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_RMS_Voltage_ C_N | 42 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Active_Power_Phase_A | 42 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Active_Power_Phase_B | 42 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Active_Power_Phase_C | 42 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Total_Active_Power | 42 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Power_Factor_Phase_A | 42 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Power_Factor_Phase_B | 42 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Power_Factor_Phase_C | 42 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT70F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pumps-8/9/10 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT70F01_Total_Power_Factor | 42 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Current_Phase_A | 43 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Current_Phase_B | 43 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Current_Phase_C | 43 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Current_Phase_Neut | 43 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Voltage_ A_N | 43 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Voltage_ B_N | 43 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_RMS_Voltage_ C_N | 43 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Active_Power_Phase_A | 43 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Active_Power_Phase_B | 43 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Active_Power_Phase_C | 43 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Total_Active_Power | 43 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Power_Factor_Phase_A | 43 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Power_Factor_Phase_B | 43 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Power_Factor_Phase_C | 43 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT80F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - 901JB003 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT80F01_Total_Power_Factor | 43 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Current_Phase_A | 44 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Current_Phase_B | 44 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Current_Phase_C | 44 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Current_Phase_Neut | 44 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Voltage_ A_N | 44 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Voltage_ B_N | 44 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_RMS_Voltage_ C_N | 44 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Active_Power_Phase_A | 44 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Active_Power_Phase_B | 44 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Active_Power_Phase_C | 44 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Total_Active_Power | 44 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Power_Factor_Phase_A | 44 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Power_Factor_Phase_B | 44 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Power_Factor_Phase_C | 44 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT81F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Lights Technical Areas - EMP109 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT81F01_Total_Power_Factor | 44 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Current_Phase_A | 45 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Current_Phase_B | 45 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Current_Phase_C | 45 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Current_Phase_Neut | 45 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Voltage_ A_N | 45 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Voltage_ B_N | 45 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_RMS_Voltage_ C_N | 45 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Active_Power_Phase_A | 45 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Active_Power_Phase_B | 45 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Active_Power_Phase_C | 45 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Total_Active_Power | 45 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Power_Factor_Phase_A | 45 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Power_Factor_Phase_B | 45 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Power_Factor_Phase_C | 45 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT82F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 1 - EMP101 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT82F01_Total_Power_Factor | 45 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Current_Phase_A | 46 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Current_Phase_B | 46 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Current_Phase_C | 46 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Current_Phase_Neut | 46 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Voltage_ A_N | 46 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Voltage_ B_N | 46 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_RMS_Voltage_ C_N | 46 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Active_Power_Phase_A | 46 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Active_Power_Phase_B | 46 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Active_Power_Phase_C | 46 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Total_Active_Power | 46 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Power_Factor_Phase_A | 46 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Power_Factor_Phase_B | 46 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Power_Factor_Phase_C | 46 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT83F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 2 - EMP102 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT83F01_Total_Power_Factor | 46 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Current_Phase_A | 47 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Current_Phase_B | 47 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Current_Phase_C | 47 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Current_Phase_Neut | 47 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Voltage_ A_N | 47 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Voltage_ B_N | 47 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_RMS_Voltage_ C_N | 47 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Active_Power_Phase_A | 47 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Active_Power_Phase_B | 47 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Active_Power_Phase_C | 47 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Total_Active_Power | 47 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Power_Factor_Phase_A | 47 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Power_Factor_Phase_B | 47 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Power_Factor_Phase_C | 47 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT84F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 3 - EMP103 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT84F01_Total_Power_Factor | 47 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Current_Phase_A | 48 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Current_Phase_B | 48 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Current_Phase_C | 48 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Current_Phase_Neut | 48 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Voltage_ A_N | 48 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Voltage_ B_N | 48 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_RMS_Voltage_ C_N | 48 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Active_Power_Phase_A | 48 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Active_Power_Phase_B | 48 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Active_Power_Phase_C | 48 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Total_Active_Power | 48 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Power_Factor_Phase_A | 48 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Power_Factor_Phase_B | 48 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Power_Factor_Phase_C | 48 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT85F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 4 - EMP104 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT85F01_Total_Power_Factor | 48 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Current_Phase_A | 49 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Current_Phase_B | 49 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Current_Phase_C | 49 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Current_Phase_Neut | 49 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Voltage_ A_N | 49 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Voltage_ B_N | 49 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_RMS_Voltage_ C_N | 49 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Active_Power_Phase_A | 49 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Active_Power_Phase_B | 49 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Active_Power_Phase_C | 49 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Total_Active_Power | 49 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Power_Factor_Phase_A | 49 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Power_Factor_Phase_B | 49 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Power_Factor_Phase_C | 49 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT86F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Captains Cabin - EMP105 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT86F01_Total_Power_Factor | 49 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Current_Phase_A | 50 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Current_Phase_B | 50 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Current_Phase_C | 50 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Current_Phase_Neut | 50 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Voltage_ A_N | 50 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Voltage_ B_N | 50 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_RMS_Voltage_ C_N | 50 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Active_Power_Phase_A | 50 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Active_Power_Phase_B | 50 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Active_Power_Phase_C | 50 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Total_Active_Power | 50 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Power_Factor_Phase_A | 50 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Power_Factor_Phase_B | 50 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Power_Factor_Phase_C | 50 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT87F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Cabin 5 - EMP106 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT87F01_Total_Power_Factor | 50 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Current_Phase_A | 51 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Current_Phase_B | 51 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Current_Phase_C | 51 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Current_Phase_Neut | 51 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Voltage_ A_N | 51 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Voltage_ B_N | 51 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_RMS_Voltage_ C_N | 51 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Active_Power_Phase_A | 51 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Active_Power_Phase_B | 51 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Active_Power_Phase_C | 51 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Total_Active_Power | 51 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Power_Factor_Phase_A | 51 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Power_Factor_Phase_B | 51 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Power_Factor_Phase_C | 51 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT88F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Laundry - EMP108 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT88F01_Total_Power_Factor | 51 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Current_Phase_A | 52 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Current_Phase_B | 52 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Current_Phase_C | 52 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Current_Phase_Neut | 52 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Voltage_ A_N | 52 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Voltage_ B_N | 52 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_RMS_Voltage_ C_N | 52 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Active_Power_Phase_A | 52 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Active_Power_Phase_B | 52 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Active_Power_Phase_C | 52 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Total_Active_Power | 52 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Power_Factor_Phase_A | 52 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Power_Factor_Phase_B | 52 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Power_Factor_Phase_C | 52 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT89F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Lounge - EMP108 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT89F01_Total_Power_Factor | 52 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Current_Phase_A | 53 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Current_Phase_B | 53 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Current_Phase_C | 53 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Current_Phase_Neut | 53 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Voltage_ A_N | 53 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Voltage_ B_N | 53 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_RMS_Voltage_ C_N | 53 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Active_Power_Phase_A | 53 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Active_Power_Phase_B | 53 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Active_Power_Phase_C | 53 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Total_Active_Power | 53 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Power_Factor_Phase_A | 53 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Power_Factor_Phase_B | 53 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Power_Factor_Phase_C | 53 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT90F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Crew Mess - EMP109 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT90F01_Total_Power_Factor | 53 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Current_Phase_A | 54 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Current_Phase_B | 54 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Current_Phase_C | 54 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Current_Phase_Neut | 54 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Voltage_ A_N | 54 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Voltage_ B_N | 54 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_RMS_Voltage_ C_N | 54 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Active_Power_Phase_A | 54 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Active_Power_Phase_B | 54 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Active_Power_Phase_C | 54 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Total_Active_Power | 54 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Power_Factor_Phase_A | 54 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Power_Factor_Phase_B | 54 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Power_Factor_Phase_C | 54 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT91F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Guest Cabin 1 - EMP112 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT91F01_Total_Power_Factor | 54 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Current_Phase_A | 55 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Current_Phase_B | 55 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Current_Phase_C | 55 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Current_Phase_Neut | 55 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Voltage_ A_N | 55 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Voltage_ B_N | 55 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_RMS_Voltage_ C_N | 55 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Active_Power_Phase_A | 55 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Active_Power_Phase_B | 55 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Active_Power_Phase_C | 55 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Total_Active_Power | 55 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Power_Factor_Phase_A | 55 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Power_Factor_Phase_B | 55 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Power_Factor_Phase_C | 55 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT92F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Dining - EMP202 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT92F01_Total_Power_Factor | 55 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Current_Phase_A | 56 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Current_Phase_B | 56 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Current_Phase_C | 56 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Current_Phase_Neut | 56 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Voltage_ A_N | 56 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Voltage_ B_N | 56 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_RMS_Voltage_ C_N | 56 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Active_Power_Phase_A | 56 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Active_Power_Phase_B | 56 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Active_Power_Phase_C | 56 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Total_Active_Power | 56 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Power_Factor_Phase_A | 56 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Power_Factor_Phase_B | 56 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Power_Factor_Phase_C | 56 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT93F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Outlets Salon - EMP201 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT93F01_Total_Power_Factor | 56 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Current_Phase_A | 57 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Current_Phase_B | 57 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Current_Phase_C | 57 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Current_Phase_Neut | 57 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Voltage_ A_N | 57 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Voltage_ B_N | 57 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_RMS_Voltage_ C_N | 57 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Active_Power_Phase_A | 57 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Active_Power_Phase_B | 57 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Active_Power_Phase_C | 57 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Total_Active_Power | 57 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Power_Factor_Phase_A | 57 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Power_Factor_Phase_B | 57 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Power_Factor_Phase_C | 57 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT94F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP110 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT94F01_Total_Power_Factor | 57 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Current_Phase_A | 58 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Current_Phase_B | 58 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Current_Phase_C | 58 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Current_Phase_Neut | 58 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Voltage_ A_N | 58 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Voltage_ B_N | 58 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_RMS_Voltage_ C_N | 58 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Active_Power_Phase_A | 58 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Active_Power_Phase_B | 58 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Active_Power_Phase_C | 58 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Total_Active_Power | 58 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Power_Factor_Phase_A | 58 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Power_Factor_Phase_B | 58 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Power_Factor_Phase_C | 58 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT95F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | EMP113 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT95F01_Total_Power_Factor | 58 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Current_Phase_A | 59 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Current_Phase_B | 59 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Current_Phase_C | 59 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Current_Phase_Neut | 59 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Voltage_ A_N | 59 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Voltage_ B_N | 59 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_RMS_Voltage_ C_N | 59 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Active_Power_Phase_A | 59 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Active_Power_Phase_B | 59 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Active_Power_Phase_C | 59 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Total_Active_Power | 59 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Power_Factor_Phase_A | 59 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Power_Factor_Phase_B | 59 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Power_Factor_Phase_C | 59 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT97F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Spare Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT97F01_Total_Power_Factor | 59 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Current_Phase_A | 60 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Current_Phase_B | 60 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Current_Phase_C | 60 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Current_Phase_Neut | 60 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Voltage_ A_N | 60 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Voltage_ B_N | 60 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_RMS_Voltage_ C_N | 60 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Active_Power_Phase_A | 60 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Active_Power_Phase_B | 60 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Active_Power_Phase_C | 60 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Total_Active_Power | 60 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Power_Factor_Phase_A | 60 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Power_Factor_Phase_B | 60 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Power_Factor_Phase_C | 60 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT98F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | KNX Supply Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT98F01_Total_Power_Factor | 60 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Current_Phase_A | 61 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Current_Phase_B | 61 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Current_Phase_C | 61 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Current_Phase_Neut | 61 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Voltage_ A_N | 61 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Voltage_ B_N | 61 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_RMS_Voltage_ C_N | 61 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Active_Power_Phase_A | 61 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Active_Power_Phase_B | 61 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Active_Power_Phase_C | 61 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Total_Active_Power | 61 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Power_Factor_Phase_A | 61 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Power_Factor_Phase_B | 61 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Power_Factor_Phase_C | 61 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT99F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AV System Supply #2 Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT99F01_Total_Power_Factor | 61 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Current_Phase_A | 62 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Current_Phase_B | 62 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Current_Phase_C | 62 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Current_Phase_Neut | 62 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Voltage_ A_N | 62 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Voltage_ B_N | 62 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_RMS_Voltage_ C_N | 62 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Active_Power_Phase_A | 62 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Active_Power_Phase_B | 62 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Active_Power_Phase_C | 62 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Total_Active_Power | 62 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Power_Factor_Phase_A | 62 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Power_Factor_Phase_B | 62 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Power_Factor_Phase_C | 62 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT111F01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | Discharge Pump Captain/Laundry Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT111F01_Total_Power_Factor | 62 | HoldingRegister | 3084 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Current Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Current_Phase_A | 63 | HoldingRegister | 3000 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Current Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Current_Phase_B | 63 | HoldingRegister | 3002 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Current Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Current_Phase_C | 63 | HoldingRegister | 3004 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Current_Phase_Neut | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Current Phase Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Current_Phase_Neut | 63 | HoldingRegister | 3006 | [7 empty] | A
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Voltage_ A_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Voltage Phase A to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Voltage_ A_N | 63 | HoldingRegister | 3028 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Voltage_ B_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Voltage Phase B to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Voltage_ B_N | 63 | HoldingRegister | 3030 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_RMS_Voltage_ C_N | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom RMS Voltage Phase C to Neutral | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_RMS_Voltage_ C_N | 63 | HoldingRegister | 3032 | [7 empty] | V
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Active_Power_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Active Power Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Active_Power_Phase_A | 63 | HoldingRegister | 3054 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Active_Power_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Active Power Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Active_Power_Phase_B | 63 | HoldingRegister | 3056 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Active_Power_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Active Power Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Active_Power_Phase_C | 63 | HoldingRegister | 3058 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Total_Active_Power | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Total Active Power | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Total_Active_Power | 63 | HoldingRegister | 3060 | [7 empty] | W
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Power_Factor_Phase_A | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Power Factor Phase A | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Power_Factor_Phase_A | 63 | HoldingRegister | 3078 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Power_Factor_Phase_B | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Power Factor Phase B | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Power_Factor_Phase_B | 63 | HoldingRegister | 3080 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Power_Factor_Phase_C | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Power Factor Phase C | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Power_Factor_Phase_C | 63 | HoldingRegister | 3082 | [7 empty] | -
R2.6 |  | Float | Powertags5 |  |  |  |  | True | PT59Q01_Total_Power_Factor | +CB.2 |  | 1000 | AC DISTR +10P3 |  | AHU2000T Crew Messroom Total Power Factor | [6 empty] | Mqtt1 | AC DISTR +10P3 | $.PT59Q01_Total_Power_Factor | 63 | HoldingRegister | 3084 | [7 empty] | -
| True | [13 empty] | Serial Interface - KEC3 Port2
| True | [13 empty] | Serial Interface - KEC3 Port3
| True | [13 empty] | Serial Interface - KEC3 Port4
| True | [13 empty] | EOF

## Help
IO list format
The Chameleon automation system can automatically read an I/O list, but it requires a fixed format. If the customer insists on different column names, we can use alias names which have to be defined custom in the software. The default format of the list:
Mandatory [1] | Name (key) |  | Description | Omschrijving
Yes | Acknowledge location |  | Location where alarm can be acknowledged. This can only be one single location, the location name can be chosen as you wish, but keep in mind to use abbreviations and use it consistently in the IO list. This will be solved by using a pull down list to choose from. | Locatie waar het alarm geaccepteerd kan worden. Dit mag slechts 1 enkele locatie zijn, de naam van de locatie is vrij te kiezen, meestal gebruiken we afkortingen. Let er wel op dat de locatie consequent juist in de lijst wordt ingevuld. Dit zal worden afgedwongen met een pull down lijst.
|  |  | For example: | Enkele voorbeelden;
|  |  | - Wheelhouse: “WH” | - Wheelhouse: “WH”
|  |  | - Engine control room: “ECR” | - Engine control room: “ECR”
|  |  | - Engine room PS: “ERPS” | - Engine room PS: “ERPS”
|  |  | - Tech space below WH: “TSBWH” | - Tech space below WH: “TSBWH”
Yes | Alarm level | HH | High-high condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “1100”. Alarm becomes active if signal > 1100 | Hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 1100. Alarm (HH) wordt dan actief bij waarde > 1100
Yes |  | H | High condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “1000”. Alarm becomes active if signal > 1000 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 1000. Alarm (H) wordt dan actief bij waarde > 1000
Yes |  | L | Low condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “600”. Alarm becomes active if signal < 600 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 600. Alarm (H) wordt dan actief bij waarde < 600
Yes |  | LL | Low-low condition setpoint (value in units of signal Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “500”. Alarm becomes active if signal < 500 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 500. Alarm (H) wordt dan actief bij waarde < 500
Yes |  | F | Setpoint for fault condition of binary I/O: “True” (for active) or “False” (for inactive). Therefore whetthe setpoint is "False" and the actual signal becomes inactive, the alarm will become active after the on delay time [Delay on] | Setpoint voor fout conditie van binaire I/O: "True" (voor actief) en "False" (voor inactief). Dus als setpoint is "False" en het signaal wordt inactief (NC), dan gaat wordt het alarm actief na het verstrijken van de off delay [Delay on]
Yes | Alert Code |  | Unique alert code, not as key for this list, but mandatory for a alarm definition | Deze unieke alert code is ontstaan om ondubbelzinnig over een alarm te kunnen communiceren en is alleen verplicht voor alarmen.
No | Cabinet |  | Cabinet number or name for selection filtering, not mandatory, therefore the syntax will not be checked. (This text will also be displayed in I/O list on screen) | Cabinet naam of nummer is hier in te vullen, deze gegevens kunnen voor selectiefilters worden gebruikt en wordt vermeld in het I/O lijst, maar er is geen invulverplichting.
No | Cable Core No |  | Core number isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Core No. (ader nummer) is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Cable ID |  | Cable id isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Cable ID is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Cable Type |  | Cable type isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Cable Type is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Call GEA on Alert |  | Automatically trigger a GEA when this alert becomes active | Veroorzaak een GEA als dit alarm actief wordt
Yes | Data Type |  | Type of data, Valid data types are: | Date type, valide types zijn:
|  |  | - Boolean: “Bool” | - Booleon: "Bool"
|  |  | - 16 bits word: “Word16” | - 16 bits word: “Word16”
|  |  | - Signed 16 bits integer: “Int16” | - Signed 16 bits integer: “Int16”
|  |  | - Unsigned 16 bits integer: “UInt16” | - Unsigned 16 bits integer: “UInt16”
|  |  | - Signed 32 bits integer: “Int32” | - Signed 32 bits integer: “Int32”
|  |  | - Unsigned 32 bits integer: “UInt32” | - Unsigned 32 bits integer: “UInt32”
|  |  | - Signed 64 bits integer: “Int64” | - Signed 64 bits integer: “Int64”
|  |  | - Floating point number: “Float” | - Floating point number: “Float”
|  |  | - Date and time: “DateTime” | - Date and time: “DateTime”
|  |  | - String of ASCII chars: “AsciiString(N)” (where N is the number of characters in the string.) | - String van ASCII chars: “AsciiString(N)” (N is het aantal karakters in de string.)
|  |  | DateTime should be a 32-bit word that counts the number of seconds since 1970-01-01T00:00:00Z. | DateTime moet een 32--bit word zijn de het aantal seconden telt vanaf 1970-01-01T00:00:00Z
|  |  | Hardwired DI and DO type signals are Bool; AI and AO are UInt16 | Bekabelde DI en DO signalen zijn van het type Boolean, AI en AO zijn Uint16
Yes | Delay On |  | Delay time for activating the alert, e.g. for 4 seconds delay: “4” | Inschakel vertraging voor het alarm in seconden, b.v. 4 sec vertraging: "4"
Yes | Deleted |  | Row has been deleted and should be ignored (mark with revision letter when row was deleted). | Deze rij is verwijderd en wordt genegeerd, maar blijft staan vanwege revisiebeheer of het is van tijdelijke aard.
Yes | Description |  | Description of signal, this tekst is also used as an alarm description, e.g. "Common alarm valve system" | Beschrijving van het signaal, deze tekst wordt ook gebruikt als alarmtext, e.g. "Algemeen alarm kleppen besturing"
Yes | Device |  | Unique identifier for device providing the IO. For example; | De unieke devicenaam waar het item bij hoort, bijvoorbeeld;
|  |  | - Hardwired:: PLC OID -> "70UP100" | - Bedraad: PLC OID -> "70UP100"
|  |  | - Serial with gateway (MB/RTU -> MB/TCP): Gateway OID -> "GW1" | - Serieel middels een gateway (MB/RTU -> MB/TCP): Gateway OID -> "GW1"
|  |  | - Serial directly to PLC comm. Kaart: PLC OID -> "70UP100" | - Serieel middels een PLC comm. Kaart: PLC OID -> "70UP100"
|  |  | - Modbus TCP/IP: MB-device OID -> "MainEngine" | - Modbus TCP/IP: MB-device OID -> "MainEngine"
Yes | Disallow Inhibit |  | Do not allow alert to be inhibited, when marked with an “X” | Sta niet toe dat dit item ge-inhibit kan worden. Gebruik bij voorkeur een "X" om aan te geven dat deze optie actief is.
No | Do Not Export |  | When not empty, item will not be exported into Codesys export files for wago | Als dit veld niet leeg is, zal dit item niet worden meegenomen in de export files voor codesys, dit veld is voorlopig specifiek voor wago plc's
No | Do Not Log |  | When not empty, item will not be logged when using datalogging | Als dit veld niet leeg is, zal dit item niet worden meegenomen in de datalogging,
No | Log to Daily Report |  | Include this I/O in the engine room report | Gebruik dit I/O in het engine room report.
Yes | General Lock[3] Tag | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | Group Alarm |  | Resound alert if input is toggled, despite being silenced. If the alarm signal is meant as a common or groupalarm, this alert can be setup to resound the it alarm horn then alarmlevel is toggled. | Opnieuw de alarm hoorn activeren als de alarm ingang opnieuw geactiveerd wordt, ondankt dat de hoorn voor dit alarm is afgezet. Als het item bedoeld is als een groepsalarm, dan kan dit alart worden ingesteld als groupsalarm, waardoor de hoorn opnieuw kan afgaan bij verandering van de ingang.
Yes | H Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | HH Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | I/O type |  | Type of I/O: | I/O type:
|  |  | - Digital input: “DI” | - Digitale input: "DI"
|  |  | - Digital output: “DO” | - Digitale output: "DI"
|  |  | - Analog input (also PT100): “AI” | - Analoge input: "AI"
|  |  | - Analog output: “AO” | - Analoge output: "AO"
|  |  | - Serial io: “SE” | - Seriële I/O: "SE"
Yes | Intended Operator Response |  | Field to provide extra information and to provide some pointers about the cause and probable solutions to fix the cause of this alert. This is a new mandatory column expected by class. For now class expects as a minimal effort to direct the operator to the operator manual. | Dit veld is bedoeld om extra informate en tips te geven omtrend dit alarm (b.v. een samenvatting uit de handleiding zijn) om de alarm situatie adequaat op te kunnen lossen. Dit is een relatief nieuwe kolom waarbij klasse in eerste in stantie minimaal een verwijzing naar het handboek verwacht.
Yes | L Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | LL Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | Modbus address |  | Modbus address for the I/O (format <word address>.<bit nr> or <bit address> in decimals) | Modbus address voor de I/O in het volgende formaat <word address>.<bit nr> or <bitaddress> allen in decimalen
Yes | Modbus function codes |  | Allowed Modbus functions at this Modbus address. Separate by comma when multiple codes are allowed. (Modbus protocol only) for modbus codes. | Modbus function code voor dit address, Als er meerdere functiecodes zijn toegestaan dan kun je die hier gescheiden door komma's invullen
Yes | Modbus slave address |  | Modbus slave address for external device. Mandatory for modbus signals | Modbus slave adres voor devices die via modbus communiceren, in dat geval it het een verplicht veld
Yes | Module |  | Device module where the IO is connected (not used for serial interface that are not connected to a [Device]) [2]. | Device module waarop het item is aangesloten. In het geval van een PLC bedoelen we de I/O kaart OID -> "DI1", deze kolom wordt niet gebruikt bij seriële signalen.
|  |  | For example: | Bijvoorbeeld:
|  |  | - The first Digital input card: “DI1” | - De eerst digitale ingangskaart: "DI1"
|  |  | - The second analog output card: “AO2” | - De tweede analoge outgangskaart: "AO2"
|  |  | - Can also be used to indicate switch OID for TCP/IP signals, e.g. "7U2" | - Kan bij TCP-IP verbindingen worden gebruikt om het switch OID aan te geven, b.v. "7U2"
Yes | OPC UA | Node ID | The unique identifier for a node in an OPC server’s address space | Het unique id voor de node dat bij dit signaal hoort in een OPC server zijn address space
Yes | OPC UA | Publish Interval | The publishi interval (in ms) is the cycle time at which a subscription executes | De publish interval is de tijd wanneer een subscription wordt uitgevoerd
No | P&ID |  | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht
Yes | Priority |  | Alarm priority type: “alarm”, “emergency”, “warning”, “caution” or empty (if unsure, use “alarm”), mandatory if item is an alarm. | Alarm prioriteit, we onderscheiden de volgende types: “alarm”, “emergency”, “warning”, “caution” of leeg laten bij geen alarm (als je het niet zeker weet, neem dan standaard “alarm”. Deze kolom is verplicht voor alarmen.
Yes | Range | Lower | Lower value of range. (Mandatory for analog signals) | Laagste waarde van de school (verplicht voor analoge signalen)
Yes |  | Upper | Upper value of range. (Mandatory for analog signals) | Hoogste waarde van de school (verplicht voor analoge signalen)
Yes | Rev |  | Last revision when the row has changed. | Revisie van de laatste wijziging
Yes | Sounding Locations |  | Additional locations where alarm buzzer should be activated, using the same location names as the acknowledge location, e.g. “WH,ECR,ERPS”. This option doen's affect the way alarms are displayed, all alarms are displayed on every workstation, bus by using samrt sorting techniques, sorting is based upon location, alert priority and timestamp. Alarms from other locations can be found further down the active alarm list or on top if there are no alarms for this location. | Additionele locaties waar de alarm hoorn ook af moet gaan als het alarm actief word, hierbij worden dezelfde locatie namen gebruikt als bij de kolom [Acknowledge location], locaties worden dan door komma's geschieden, b.v.; "WH,ECR,ERPS". Deze optie heeft niets te maken met het tonen van alarmen. Alle alarmen worden op alle workstations getoond, maar door slimme sorteermethodes worden de alarmen gesorteerd wordt op locatie, alert prioriteit en tijdsstempel.
Yes | System |  | Used for sorting by system, when using this column, system grouping can be used, for instance in the I/O maintenance screen. Intended to be a short description e.g. "ME PS" or "FAS" or "TMS". Max 16 characters. | Wordt gebruikt voor het sorteren van de items, bijvoorbeeld in het I/O lijst scherm onder maintenance. Bedoeld als korte omschrijving, bijv. "ME PS" of "FAS" of "TMS". Max 16 karacters.
Yes | Tag |  | Unique IO identifier (Composed of an SFI code and an abbreviation for the function) | Uniek id voor dit signaal, dit mag een SFI codering zijn of in de meeste gevallen iets beschrijvends, zoals "CommonAlarm"
Yes | Is Subscribe |  | Define if the line is a subscribe to another Tag in the I/O List. | Specificeert of the lijn “subscribed” op een andere lijn in de I/O lijst
Yes | Prefix Device |  | The tag will be published in our system with the device as a prefix | De tag wordt gepubliseerd met de devicenaam als voorvoegsel in ons systeem
Yes | Terminal |  | To further specify the signals connected to the [Module], use the input number of the i/o module mentioned in column [Module], e.g. third input on DI: “3” | Deze kolom is bedoeld ter aanvulling van de kolom [Module], hier geef je aan op welke in- of uitgang van de [Module] het signaal is aangesloten, b.v. derde input op DI2: "3"
|  |  | For serial interfaces: | Voor seriële interfaces:
|  |  | - With gateway: Port number on gateway e.g. "2" | - Bij gebruik van een Gateway: Poortnummer op gateway, b.v. "2"
|  |  | - Directly to PLC: not used | - Direct op een [Device] zonder module, b.v. "X2"
|  |  | - Modbus TCP/IP: Port number on switch, e.g. "3" | - Kan bij TCP/IP verbindingen worden gebruikt voor poortnummer op switch, b.v. "1"
No | Timestamp |  | Workstation of last change in io item | Geeft aan op welk werkstation de laatste wijziging is gedaan
Yes | Unit |  | Unit of the measured value. For example; Bar, mA | Eenheid van het te meten signaal. Bijvoorbeeld Bar, mA, wordt o.a. gebruikt voor trending
Yes | VDR ID |  | Send all changes to voyage data recorder. Mark with unique ID number, which will also be send to the VDR system. Leaving the column empty means, VDR notification is not applicable | Middels deze kolom is aan te geven of het alarm doorgezet moet worden naar het VDR systeem, waar van toepassing. Als deze kolom niet leeg is, is het doorsturen van toepassing. Gebruik bij voorkeur een unit id nummer welke meegezonden wordt naar de VDR.
No | Workstation |  | Do not used, colums is used by system to indicate workstation of last change in io item | Niet gebruiken, deze kolom wordt door het systeem gebruikt om aan te geven op welk werkstation de laatste wijziging is gedaan
No | Yard Tag |  | Informative item for separated Yard id numbering or e.g. for SFI coding | Informatief veld voor b.v. aparte werfcondering of SFI codering.
Additional columns are allowed, if the column is not defined in the list above, it will be ignored. Examples are; - Green line (level for green line on gauge to indicate nominal value) - Red line (for max level) - Specific ID's - Extended cabinet name / location - Eplan coding - Prefix - etc. |  |  |  | Meer kolommen toevoegen voor meer detailering / extra informatie of kruisverwijzingen is geen probleem, onbekende kolommen worden genegeerd. Bijvoorbeeld; - Green line (nominale niveau die met een groene lijn op een meter wordt aangegeven) - Red line (max niveau die je aan aangeven met een rode lijn) - Kruisverwijzingen / ID's - Uitgebreidere omschrijvingen van panelen en locaties - Prefix - etc.
[1] Mandatory columns can be empty, but they have to be defined in the I/O list

## Internal lists
Direction | Data Type | Alert Priority | Lock Operator | True False | Modbus Data Type | Module Type
In | Bool | Emergency | < | True | Coil | ReadFieldbus
InOut | Int16 | Alarm | > | False | Input | WriteFieldbus
Out | Int32 | Warning | = |  | InputRegister | ReadWriteFieldbus
| Int64 | Caution |  |  | HoldingRegister | RetainPersistent
| UInt16 | Event |  |  |  | Other
| UInt32 |  |  |  |  | 750-403
| UInt64 |  |  |  |  | 750-430
| Float |  |  |  |  | 750-454
| Double |  |  |  |  | 750-455
| DateTime |  |  |  |  | 750-461
| TimeSpan |  |  |  |  | 750-461/000-003
| UnixDateTime |  |  |  |  | 750-464#02-RTD-PT
| String |  |  |  |  | 750-485
| AsciiString |  |  |  |  | 750-511/000-001
| IpAddress |  |  |  |  | 750-511/000-002
| Blob |  |  |  |  | 750-517
750-530
750-554
750-555
750-610
750-1400
750-1415
750-1425
750-1500
750-1515