## Rev
Revision | Description / Remarks
R0.0 | Initial release from template for Project Zero
R0.1 | IO-list according single line version R1.5 - dd 2023-11-14
R0.2 | Re-arranged columns acc. standard. - dd. 2023-11-22 Essential IO (Internal) transferred to PMS Io-list (UMS entrance, acc. Alarm panels) dd. 2023-11-24 Update acc. comments yard - dd. 2023-11-21
R0.3 | Adjusted to latest System Overview R1.6. (ASI interface moved from AMCS KEB3 to PMS IO list KEB4) - dd 2023-12-01
R0.4 | Adjusted to the latest System Overview R1.7. Deleted KEB 3 in the main saloon. - dd. 2024-02-07 Also moved internal IO from KEB3 to KEB2 for "Bridge" silence and buzzer connection
R1.0 | Added Alewijnse AC board IO (Pump control) dd. 5-03-2023
R1.1 | Name of the list adjusted to the detailed engineering project number - dd 04-04-2024 Adjusted the IO-locations of the water sensors to CB.02 - dd 04-04-2024 Changed system numbers BUMO to the yard system numbers 05-04-2024 Added fresh water system 05-04-2024
R1.2 | Added Tijssen Monitor Switching per location. 16-04-2024
R1.3 | Final Bilge & Fifi info based on Multinlines Alewijnse 2-05-2024 Added DE and Nde Pt100 readouts of propulsion motors (16-05-2024)
R1.4 | Added internal IO
R1.5 | Added Accelleration sensors 1x MTS & 1x Crew. (3-06-2024) Hull temperature Activation output added in CB.01 (04-06-2024) Added pneumatic prseeure sensor (11-06-2024)
R1.6 | IO card rename
R1.7 | Added Grey & Black Water System (04-07-2024) Changed the 750-461 pt100 cards to 750-450#2 cards in consultancy with Wouter. Added Deck Equipment Deck Crane inputs (04-07-2024)
R1.8 | Updated project to latest release, updated IO list to work with latest release and minimize validation failures in software
R1.9 | Wago 750-450 card update
R1.10 | Added "Sideboarding platform crew (PS) Closed & Locked" for Doors & hatches system - dd 08-10-2024 Added fire detection fault input dd 11-10-2024 Added KEB1 DO61 output card dd 15-10-2024 Battery Ventilation IO added dd 15-10-2024 Watertight hinged doors IO added dd 17-10-2024 Added KEB1 DO62 output card for Locker, FP & Laz Ventilation dd 28-10-2024 Added KEB1 DI30 4-20mA input card dd 29-10-2024
R1.11 | Added IO for Fire Dampers MTS Ventilation dd.4-11-2024

## Project definitions
Devices | Cabinet | Systems | Locations
PHW1 | 70.51 Alarm Cabinet WH | AMCS | BRG
PHW2 | 70.52 Alarm Cabinet TS | EMS | ER
PHW3 | 70.53 Alarm Cabinet ER | BMS | TS
PHU1 |  | PCS
PHU2 |  | HEALTH
KEB1 |  | PAT
KEB2 |  | TMS
KEB3 |  | Modbus
KEB4 |  | VPS
KEB5
KEF1
KEF2
BRG
ER
TS
Health
UAP
VIRT-KFE1
VIRT-KFE2
VIRT-PHW
TMS
SoftPLC
NAVLIGHTS
Alarming
PHU3
SystemHealthMonitor
WagoPlcAdapter
UapServer
MdbsSrvTst
MdbsClntTst

## IO-List
Rev. | Deleted | Target Type | Device | Module | Module Type | Terminal | Is Subscribe | Prefix Device | Tag | Cabinet | System | Yard Tag | Description | Parent | Redundant tag | P&ID | Cable |  |  | OPC UA |  | Modbus | [7 empty] | Range |  | Unit | Precision | Alert Code | Alert |  |  |  |  | Delay On | Acknowledge Location | Sounding Locations | Alert priority | Intended Operator Response | Category A | Group Alarm | Call GEA on Alert | Disallow Inhibit | Vdr ID | General Lock |  |  | HH Lock |  |  | H Lock |  |  | L Lock |  |  | LL Lock |  |  | Do Not Log | Log To Daily Report | Log to CDP | Workstation | Timestamp
[17 empty] | ID | Type | Core No. | Node ID | Publish Interval | Slave Address | Data Type | Address | Source Type | Byte Size | Swap Words | Lower | Upper | Lower | Upper |  |  |  | HH | H | L | LL | F | [10 empty] | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level | Tag | Operator | Level
| True | [11 empty] | ALARM CABINET - AMCS Main technical Space +CB.1
R1.8 |  | Bool | KEB1 | DI00 | 750-1415 | 1 |  |  | AmcsPowerSupplyFailure | DSK_SWR | 4500 AMCS |  | MTS AMCS 1 Power Supply Failure | [20 empty] | 4 |  |  |  |  | False |  | TS |  | Alarm | Check Primary (G2) supply, Secundary (G3) supply and redundancy module (G1) |  |  |  |  | 1
R1.9 |  | Bool | KEB1 | DI00 | 750-1415 | 2 |  |  | Spare_DI00_2 | DSK_SWR | 4500 AMCS |  | Spare | [20 empty] | 5 |  |  |  |  | False |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 3 |  |  | UmsEntranceUnitMannedSwitch | DSK_SWR | 4500 AMCS |  | UMS Entrance Unit Manned Switch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 4 |  |  | UmsEntranceUnitUnmannedSwitch | DSK_SWR | 4500 AMCS |  | UMS Entrance Unit Unmanned Switch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 5 |  |  | UmsEntranceUnitOneManSwitch | DSK_SWR | 4500 AMCS |  | UMS Entrance Unit One Man Switch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 6 |  |  | UmsEntranceUnitMoreMenSwitch | DSK_SWR | 4500 AMCS |  | UMS Entrance Unit More Men Switch
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 7 |  |  | UmsOneManTimerResetButton | DSK_SWR | 4500 AMCS |  | UMS One Man Timer Reset Button
R0.0 |  | Bool | KEB1 | DI00 | 750-1415 | 8 |  |  | Spare_DI00_8 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 1 |  |  | AlarmPanelSilenceButton | DSK_SWR | 4500 AMCS |  | Alarm Panel Silence Button
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 2 |  |  | Spare_DI01_2 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 3 |  |  | AlarmPanelGeaCallRevokeButton | DSK_SWR | 4500 AMCS |  | Alarm Panel GEA CallRevoke Button
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 4 |  |  | AlarmPanelAcknowledgeButton | DSK_SWR | 4500 AMCS |  | Alarm Panel Acknowledge Button
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 5 |  |  | Spare_DI01_5 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 6 |  |  | Spare_DI01_6 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 7 |  |  | Spare_DI01_7 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DI01 | 750-1415 | 8 |  |  | Spare_DI01_8 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 1 |  |  | UmsMannedLight | DSK_SWR | 4500 AMCS |  | UMS Manned Light
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 2 |  |  | UmsTimingOnLight | DSK_SWR | 4500 AMCS |  | UMS Timing On Light
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 3 |  |  | Spare_DO00_3 | DSK_SWR | 4500 AMCS |  | Spare
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 4 |  |  | UmsOneManTimerResetLight | DSK_SWR | 4500 AMCS |  | UMS One Man Timer Reset Light
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 5 |  |  | AlarmPanelSilenceLight | DSK_SWR | 4500 AMCS |  | Alarm Panel Silence Light
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 6 |  |  | AlarmPanelGeaCallRevokeLight | DSK_SWR | 4500 AMCS |  | Alarm Panel GEA CallRevoke Light
R1.9 |  | Bool | KEB1 | DO00 | 750-1515 | 7 |  |  | MachinerySpaceBuzzerHorn | DSK_SWR | 4500 AMCS |  | Machinery Space Buzzer Horn
R0.0 |  | Bool | KEB1 | DO00 | 750-1515 | 8 |  |  | AlarmPanelAcknowledgeLight | DSK_SWR | 4500 AMCS |  | Alarm Panel Acknowledge Light
R1.8 |  | Bool | KEB1 | F1 | 750-610 | 1 |  |  | AmcsPlcPowerModule1InternalFuseBlown | DSK_SWR | 4500 AMCS |  | AMCS PLC KEB1 Power Module 1 Internal Fuse Blown | [20 empty] | 28 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | F1 | 750-610 | 2 |  |  | AmcsPlcPowerModule1PowerFailure | DSK_SWR | 4500 AMCS |  | AMCS PLC KEB1 Power Module 1 Power Failure | [20 empty] | 29 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 1 |  |  | BILGE_LEVEL_SUB_PUMP1_ALARM | +CB.1 | 2100 BILGE FIFI | 21001048_1 | Water Sensor for Submersible Pump 1 Alarm |  |  |  | 381W0039
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 2 |  |  | BILGE_LEVEL_SUB_PUMP2_ALARM | +CB.1 | 2101 BILGE FIFI | 21001048_2 | Water Sensor for Submersible Pump 2 Alarm |  |  |  | 381W0040
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 3 |  |  | BILGE_LEVEL_SUB_PUMP3_ALARM | +CB.1 | 2102 BILGE FIFI | 21001048_3 | Water Sensor for Submersible Pump 3 Alarm |  |  |  | 381W0041
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 4 |  |  | GEN_SERV_PUMP1_REM_AVAIL | +CB.1 | 2100 GENERAL SERVICE | 21001001 | General Service Pump 1 Remote Available |  |  |  | 381W0005
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 5 |  |  | GEN_SERV_PUMP2_REM_AVAIL | +CB.1 | 2100 GENERAL SERVICE | 21001002 | General Service Pump 2 Remote Available |  |  |  | 381W0004
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 6 |  |  | GEN_SERV_PUMP2_FIELD_START | +CB.1 | 2100 GENERAL SERVICE |  | General Service Pump 2 Field Start |  |  |  | 381W0003
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 7 |  |  | GEN_SERV_PUMP2_FIELD_STOP | +CB.1 | 2100 GENERAL SERVICE |  | General Service Pump 2 Field Stop
R1.0 |  | Bool | KEB1 | DI20 | 750-1415 | 8 |  |  | STRIP_PUMP_REM_AVAIL | +CB.1 | 2100 BILGE FIFI | 21001004 | Stripping Pump Remote Available |  |  |  | 381W0010
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 1 |  |  | STRIP_PUMP_RUNNING | +CB.1 | 2100 BILGE FIFI |  | Stripping Pump Running
R1.6 |  | Bool | KEB1 | DI21 | 750-1415 | 2 |  |  | GEN_SERV_PUMP1_REM_START | +CB.1 | 2100 GENERAL SERVICE | 21001001 | General Service Pump 1 Remote Start / Running |  |  |  | 381W0005
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 3 |  |  | CHAIN_LOCK_PUMP_REM_AVAIL | +CB.1 | 2100 BILGE FIFI | 21001005 | Chain Locker Pump Remote Available
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 4 |  |  | CHAIN_LOCK_PUMP_RUNNING | +CB.1 | 2100 BILGE FIFI |  | Chain Locker Pump Running
R1.6 |  | Bool | KEB1 | DI21 | 750-1415 | 5 |  |  | GEN_SERV_PUMP2_REM_START | +CB.1 | 2100 GENERAL SERVICE | 21001002 | General Service Pump 2 Remote Start / Running |  |  |  | 381W0087
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 6 |  |  | SUBMERS_PUMP1_REM_AVAIL | +CB.1 | 2100 BILGE FIFI | 21001006-1 | Submersible Pump 1 Remote Available |  |  |  | 381W0009
R1.0 |  | Bool | KEB1 | DI21 | 750-1415 | 7 |  |  | SUBMERS_PUMP1_RUNNING | +CB.1 | 2100 BILGE FIFI |  | Submersible Pump 1 Running
R1.3 |  | Bool | KEB1 | DI21 | 750-1415 | 8 |  |  | Spare_DI21_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 1 |  |  | SUBMERS_PUMP2_REM_AVAIL | +CB.1 | 2100 BILGE FIFI | 21001006-2 | Submersible Pump 2 Remote Available |  |  |  | 381W0085
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 2 |  |  | SUBMERS_PUMP2_RUNNING | +CB.1 | 2100 BILGE FIFI |  | Submersible Pump 2 Running
R1.3 |  | Bool | KEB1 | DI22 | 750-1415 | 3 |  |  | Spare_DI22_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 4 |  |  | SUBMERS_PUMP3_REM_AVAIL | +CB.1 | 2100 BILGE FIFI | 21001006-3 | Submersible Pump 3 Remote Available |  |  |  | 381W0009
R1.0 |  | Bool | KEB1 | DI22 | 750-1415 | 5 |  |  | SUBMERS_PUMP3_RUNNING | +CB.1 | 2100 BILGE FIFI |  | Submersible Pump 3 Running
R1.3 |  | Bool | KEB1 | DI22 | 750-1415 | 6 |  |  | Spare_DI22_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.8 |  | Bool | KEB1 | DI22 | 750-1415 | 7 |  |  | FRESH_WATER_MAK1_ALARM | +CB.1 | 2500 FRESH WATER | 25001001_1 | Fresh Water Maker 1 Common Alarm |  |  |  | 421.1W0003 | [16 empty] | 52 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI22 | 750-1415 | 8 |  |  | FRESH_WATER_MAK2_ALARM | +CB.1 | 2500 FRESH WATER | 25001001_2 | Fresh Water Maker 2 Common Alarm |  |  |  | 421.1W0006 | [16 empty] | 53 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | DI23 | 750-1415 | 1 |  |  | FRESH_WATER_CHLORINE_UNIT_ALARM | +CB.1 | 2500 FRESH WATER | 25001017 | Chlorine Dosing Unit Common Alarm |  |  |  | 421.1W0010 | [16 empty] | 54 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 2 |  |  | TRANS_PUMP_BLCK_WAT_REM_AVAIL | +CB.1 | 3400 SEWAGE | 34001001 | Transfer Pump 2 Black Water Remote Available |  |  |  | 447W0004
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 3 |  |  | TRANS_PUMP_BLCK_WAT_RUNNING | +CB.1 | 3400 SEWAGE |  | Transfer Pump 2 Black Water Running
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 4 |  |  | TRANS_PUMP_GREY_WAT_REM_AVAIL | +CB.1 | 3400 SEWAGE | 34001002 | Transfer Pump 1 Gray Water Remote Available |  |  |  | 447W0007
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 5 |  |  | TRANS_PUMP_GREY_WAT_RUNNING | +CB.1 | 3400 SEWAGE |  | Transfer Pump 1 Gray Water Running
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 6 |  |  | PUMP_FWD_GREY_WAT_REM_AVAIL | +CB.1 | 3400 SEWAGE | 34001003 | Pump 3 Fwd Grey Water Remote Available |  |  |  | 447W0004
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 7 |  |  | PUMP_FWD_GREY_WAT_RUNNING | +CB.1 | 3400 SEWAGE |  | Pump 3 Fwd Grey Water Running
R1.7 |  | Bool | KEB1 | DI23 | 750-1415 | 8 |  |  | SEW_TREAT_RUNNING | +CB.1 | 3400 SEWAGE |  | Sewage Treatment Plant Running
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 1 |  |  | SEW_TREAT_RELEASE | +CB.1 | 3400 SEWAGE |  | Sewage Treatment Plant Release
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 2 |  |  | SEW_TREAT_GEN_ALARM | +CB.1 | 3400 SEWAGE |  | Sewage Treatment Plant General Alarm
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 3 |  |  | Spare_DI24_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 4 |  |  | SEW_TREAT_DRY_RUNN_PROT | +CB.1 | 3400 SEWAGE |  | Sewage Treatment Plant Dry Running Protection & Cleaning Pum[
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 5 |  |  | PASS_HATCH_CL_LOCK | +CB.1 | 7500 PASSERELLE |  | Passerelle Hatch Closed & Locked |  |  |  | 537W0002
R1.7 |  | Bool | KEB1 | DI24 | 750-1415 | 6 |  |  | SBL_SB_CLOSED_LOCKED | +CB.1 | 7500 BOARDING LADDER |  | SB Side Boarding Ladder Closed & Locked |  |  |  | 543W0002
R0.1 |  | Bool | KEB1 | DI24 | 750-1415 | 7 |  |  | SBL_SPARE_INPUT | +CB.1 | 7500 BOARDING LADDER |  | Side Boarding Ladder Spare
R1.10 |  | Bool | KEB1 | DI24 | 750-1415 | 8 |  |  | NOVEC_RELEASED_ALARM | +CB.1 | 2200 NOVEC |  | Novec Released |  |  |  | 401.2W0004 | 2x2x0.75 | [15 empty] | 69 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 1 |  |  | TECH_CORRIDOR_ESC_HATCH_SB | +CB.1 | 0900 DOORS HATCHES |  | Technical Corridor Escape Hatch SB Nr.27 |  |  |  | 535W0016
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 2 |  |  | TECH_ROOM_ESC_HATCH_PS | +CB.1 | 0900 DOORS HATCHES |  | Technical Room Escape Hatch PS Nr.31 |  |  |  | 535W0018
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 3 |  |  | MAIN_DECKH_VENT_HATCH_SB | +CB.1 | 0900 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch SB Nr.33 |  |  |  | 535W0020
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 4 |  |  | MAIN_DECKH_VENT_HATCH_PS | +CB.1 | 0900 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch PS Nr.34 |  |  |  | 535W0022
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 5 |  |  | MAIN_DECKH_ACCESS_DOOR | +CB.1 | 0900 DOORS HATCHES |  | Main Deckhouse Access Door Nr.35 |  |  |  | 535W0024
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 6 |  |  | AFT_DECKH_ACCESS_DOOR | +CB.1 | 0900 DOORS HATCHES |  | Aft Deckhouse Access Door Nr.36 |  |  |  | 535W0026
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 7 |  |  | LAZA_ACCESS_HATCH_SB_FWD | +CB.1 | 0900 DOORS HATCHES |  | Lazarette Access Hatch SB Fwd Nr.37 |  |  |  | 535W0028
R1.7 |  | Bool | KEB1 | DI25 | 750-1415 | 8 |  |  | LAZA_ACCESS_HATCH_PS_FWD | +CB.1 | 0900 DOORS HATCHES |  | Lazarette Access Hatch PS Fwd Nr.38 |  |  |  | 535W0030
R1.7 |  | Bool | KEB1 | DI26 | 750-1415 | 1 |  |  | LAZA_ACCESS_HATCH_SB_MID | +CB.1 | 0900 DOORS HATCHES |  | Lazarette Access Hatch SB Mid Nr.39 |  |  |  | 535W0032
R1.7 |  | Bool | KEB1 | DI26 | 750-1415 | 2 |  |  | LAZA_ACCESS_HATCH_PS_MID | +CB.1 | 0900 DOORS HATCHES |  | Lazarette Access Hatch PS Mid Nr.40 |  |  |  | 535W0034
R1.7 |  | Bool | KEB1 | DI26 | 750-1415 | 3 |  |  | LAZA_ACCESS_HATCH_SB_AFT | +CB.1 | 0900 DOORS HATCHES |  | Lazarette Access Hatch SB Aft Nr.41 |  |  |  | 535W0036
R1.7 |  | Bool | KEB1 | DI26 | 750-1415 | 4 |  |  | LAZA_ACCESS_HATCH_PS_AFT | +CB.1 | 0900 DOORS HATCHES |  | Lazarette Access Hatch PS Aft Nr.42 |  |  |  | 535W0040
R1.7 |  | Bool | KEB1 | DI26 | 750-1415 | 5 |  |  | AFT_DECKH_VENT_HATCH | +CB.1 | 0900 DOORS HATCHES |  | Aft Deckhouse Ventilation Hatch Nr.44 |  |  |  | 535W0042
R1.10 |  | Bool | KEB1 | DI26 | 750-1415 | 6 |  |  | SBP_PS_CLOSED_LOCKED | +CB.1 | 0900 DOORS HATCHES |  | PS Sideboarding Platform Crew Closed & Locked
R1.10 |  | Bool | KEB1 | DI26 | 750-1415 | 7 |  |  | VENT_SUPP_TECH_SPACE_REM_AVAIL | +CB.1 | 3500 VENTILATION |  | Ventilation Supply Technical Space Remote Available
R1.10 |  | Bool | KEB1 | DI26 | 750-1415 | 8 |  |  | VENT_SUPP_TECH_SPACE_RUNNING | +CB.1 | 3500 VENTILATION |  | Ventilation Supply Technical Space Running
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 1 |  |  | VENT_EXTR_TECH_SPACE_REM_AVAIL | +CB.1 | 3500 VENTILATION |  | Ventilation Extractor Technical Space Remote Available
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 2 |  |  | VENT_EXTR_TECH_SPACE_RUNNING | +CB.1 | 3500 VENTILATION |  | Ventilation Extractor Technical Space Running
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 3 |  |  | BATT_VENT_AFT_PS_ON_RUN | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT PS On / Run |  |  |  | 412.3W0023
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 4 |  |  | BATT_VENT_AFT_PS_ON_FAULT | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT PS Fault | [20 empty] | 89 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 5 |  |  | BATT_VENT_AFT_PS_ON_READY | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT PS Ready
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 6 |  |  | BATT_VENT_AFT_SB_ON_RUN | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT SB On / Run |  |  |  | 412.3W0024
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 7 |  |  | BATT_VENT_AFT_SB_ON_FAULT | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT SB Fault | [20 empty] | 92 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB1 | DI27 | 750-1415 | 8 |  |  | BATT_VENT_AFT_SB_ON_READY | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT SB Ready
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 1 |  |  | DRAIN_VLV_Y01_POS_OVERBOARD | +CB.1 | 2500 TECHWATER | 25004014_1 | Drain water Valve Y01 Position Overboard |  |  |  | 421.2W0009 | 2x2x0,75
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 2 |  |  | DRAIN_VLV_Y01_POS_TO_PURO | +CB.1 | 2500 TECHWATER | 25004014_1 | Drain water Valve Y01 Position to Puro
R1.10 |  | Bool | KEB1 | DI28 | 750-1415 | 3 |  |  | TECH_WATER_CHLORINE_UNIT_ALARM | +CB.1 | 2500 TECHWATER | 25004035 | Chlorine Dosing Unit Common Alarm |  |  |  | 421.2W0020 | 2x2x0,75 | [15 empty] | 96 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 4 |  |  | MTS_INLET_FIRE_FLAP_RELEASED | +CB.1 | 3500 VENTILATION | 35005031_1 | Main Technical Space Inlet Fire Flap Released |  |  |  | 415W0004 | SPEC_CAB | [15 empty] | 97 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 5 |  |  | MTS_INLET_FIRE_FLAP_FULLY_RESET | +CB.1 | 3500 VENTILATION | 35005031_1 | Main Technical Space Inlet Fire Flap Fully Reset
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 6 |  |  | MTS_EXHAUST_FIRE_FLAP_RELEASED | +CB.1 | 3500 VENTILATION | 35005031_2 | Main Technical Space Exhaust Fire Flap Released |  |  |  | 415W0006 | SPEC_CAB | [15 empty] | 99 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.11 |  | Bool | KEB1 | DI28 | 750-1415 | 7 |  |  | MTS_EXHAUST_FIRE_FLAP_FULLY_RESET | +CB.1 | 3500 VENTILATION | 35005031_2 | Main Technical Space Exhaust Fire Flap Fully Reset
R0.1 |  | Bool | KEB1 | DI28 | 750-1415 | 8 |  |  | Spare_DI28_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 1 |  |  | Spare_DI29_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 2 |  |  | Spare_DI29_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 3 |  |  | Spare_DI29_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 4 |  |  | Spare_DI29_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 5 |  |  | Spare_DI29_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 6 |  |  | Spare_DI29_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 7 |  |  | Spare_DI29_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI29 | 750-1415 | 8 |  |  | Spare_DI29_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 1 |  |  | Spare_DI30_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 2 |  |  | Spare_DI30_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 3 |  |  | Spare_DI30_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 4 |  |  | Spare_DI30_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 5 |  |  | Spare_DI30_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 6 |  |  | Spare_DI30_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 7 |  |  | Spare_DI30_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI30 | 750-1415 | 8 |  |  | Spare_DI30_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 1 |  |  | Spare_DI31_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 2 |  |  | Spare_DI31_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 3 |  |  | Spare_DI31_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 4 |  |  | Spare_DI31_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 5 |  |  | Spare_DI31_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 6 |  |  | Spare_DI31_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 7 |  |  | Spare_DI31_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI31 | 750-1415 | 8 |  |  | Spare_DI31_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 1 |  |  | Spare_DI32_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 2 |  |  | Spare_DI32_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 3 |  |  | Spare_DI32_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 4 |  |  | Spare_DI32_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 5 |  |  | Spare_DI32_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 6 |  |  | Spare_DI32_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 7 |  |  | Spare_DI32_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI32 | 750-1415 | 8 |  |  | Spare_DI32_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 1 |  |  | Spare_DI33_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 2 |  |  | Spare_DI33_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 3 |  |  | Spare_DI33_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 4 |  |  | Spare_DI33_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 5 |  |  | Spare_DI33_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 6 |  |  | Spare_DI33_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 7 |  |  | Spare_DI33_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI33 | 750-1415 | 8 |  |  | Spare_DI33_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 1 |  |  | Spare_DI34_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 2 |  |  | Spare_DI34_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 3 |  |  | Spare_DI34_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 4 |  |  | Spare_DI34_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 5 |  |  | Spare_DI34_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 6 |  |  | Spare_DI34_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 7 |  |  | Spare_DI34_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI34 | 750-1415 | 8 |  |  | Spare_DI34_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 1 |  |  | Spare_DI35_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 2 |  |  | Spare_DI35_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 3 |  |  | Spare_DI35_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 4 |  |  | Spare_DI35_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 5 |  |  | Spare_DI35_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 6 |  |  | Spare_DI35_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 7 |  |  | Spare_DI35_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI35 | 750-1415 | 8 |  |  | Spare_DI35_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 1 |  |  | Spare_DI36_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 2 |  |  | Spare_DI36_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 3 |  |  | Spare_DI36_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 4 |  |  | Spare_DI36_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 5 |  |  | Spare_DI36_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 6 |  |  | Spare_DI36_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 7 |  |  | Spare_DI36_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI36 | 750-1415 | 8 |  |  | Spare_DI36_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 1 |  |  | Spare_DI37_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 2 |  |  | Spare_DI37_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 3 |  |  | Spare_DI37_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 4 |  |  | Spare_DI37_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 5 |  |  | Spare_DI37_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 6 |  |  | Spare_DI37_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 7 |  |  | Spare_DI37_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI37 | 750-1415 | 8 |  |  | Spare_DI37_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 1 |  |  | Spare_DI38_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 2 |  |  | Spare_DI38_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 3 |  |  | Spare_DI38_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 4 |  |  | Spare_DI38_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 5 |  |  | Spare_DI38_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 6 |  |  | Spare_DI38_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 7 |  |  | Spare_DI38_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI38 | 750-1415 | 8 |  |  | Spare_DI38_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 1 |  |  | Spare_DI39_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 2 |  |  | Spare_DI39_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 3 |  |  | Spare_DI39_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 4 |  |  | Spare_DI39_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 5 |  |  | Spare_DI39_5_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 6 |  |  | Spare_DI39_6_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 7 |  |  | Spare_DI39_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DI39 | 750-1415 | 8 |  |  | Spare_DI39_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.8 |  | Float | KEB1 | AI20 | 750-455 | 1 |  |  | FLOW_LOWER_SALOON_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_30 | Flow Sensor Lower Saloon Cold Water |  |  |  | 421.1W0146 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI20 | 750-455 | 2 |  |  | FLOW_DAYHEAD_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_31 | Flow Sensor Dayhead Cold Water |  |  |  | 421.1W0147 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI20 | 750-455 | 3 |  |  | FLOW_GUEST_CABIN_SB_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001037_33 | Flow Sensor Guest Cabin SB Hot Water |  |  |  | 421.1W0148 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI20 | 750-455 | 4 |  |  | FLOW_GUEST_CABIN_SB_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_32 | Flow Sensor Guest Cabin SB Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI21 | 750-455 | 1 |  |  | FLOW_GUEST_CABIN_PS_FWD_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001037_36 | Flow Sensor Guest Cabin PS Fwd Hot Water |  |  |  | 421.1W0149 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI21 | 750-455 | 2 |  |  | FLOW_GUEST_CABIN_PS_FWD_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_34 | Flow Sensor Guest Cabin PS Fwd Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI21 | 750-455 | 3 |  |  | FLOW_GUEST_CABIN_PS_AFT_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001037_38 | Flow Sensor Guest Cabin PS Aft Hot Water |  |  |  | 421.1W0150 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI21 | 750-455 | 4 |  |  | FLOW_GUEST_CABIN_PS_AFT_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_35 | Flow Sensor Guest Cabin PS Aft Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI22 | 750-455 | 1 |  |  | FLOW_MASTER_CABIN_SB_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001037_40 | Flow Sensor Master Cabin SB Hot Water |  |  |  | 421.1W0151 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI22 | 750-455 | 2 |  |  | FLOW_MASTER_CABIN_SB_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_37 | Flow Sensor Master Cabin SB Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI22 | 750-455 | 3 |  |  | FLOW_MASTER_CABIN_PS_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001037_42 | Flow Sensor Master Cabin PS Hot Water |  |  |  | 421.1W0074 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI22 | 750-455 | 4 |  |  | FLOW_MASTER_CABIN_PS_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_39 | Flow Sensor Master Cabin PS Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI23 | 750-455 | 1 |  |  | FLOW_LAZARET_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001037_43 | Flow Sensor Lazaret Hot Water |  |  |  | 421.1W0075 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI23 | 750-455 | 2 |  |  | FLOW_LAZARET_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_41 | Flow Sensor Lazaret Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI23 | 750-455 | 3 |  |  | FLOW_WATER_SOFTNER_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001124 | Flow Sensor Water Softner Cold Water |  |  |  | 421.1W0080 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI23 | 750-455 | 4 |  |  | FLOW_MAIN_TECH_SPACE_HOT_WATER | +CB.1 | 2500 FRESH WATER | 25001123_1 | Flow Sensor Main Technical Space Hot Water |  |  |  | 421.1W0159 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 1 |  |  | FLOW_MAIN_TECH_SPACE_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001037_1 | Flow Sensor Main Technical Space Cold Water |  |  |  | 421.1W0160 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 2 |  |  | FLOW_MAIN_TECH_SPACE_FR45_COLD_WATER | +CB.1 | 2500 FRESH WATER | 25001123_2 | Flow Sensor Main Technical Space FR45 Bilge Area Cold Water |  |  |  | 421.1W0162 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 3 |  |  | LEVEL_FRESH_WATER_TANK_1_FR_45_PS | +CB.1 | 2500 FRESH WATER | 25001019_1 | Level Sensor Fresh Water Tank 1 FR 45 PS |  |  |  | 421.1W0088 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI24 | 750-455 | 4 |  |  | LEVEL_FRESH_WATER_TANK_2_FR_45_SB | +CB.1 | 2500 FRESH WATER | 25001019_2 | Level Sensor Fresh Water Tank 2 FR 45 SB |  |  |  | 421.1W0089 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI25 | 750-455 | 1 |  |  | TEMP1_FOR_ENERGY_REC_SYSTEM | +CB.1 | 2500 FRESH WATER | 25001038_1 | Temperature Sensor 1 For Energy Recovery System |  |  |  | 421.1W0090 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI25 | 750-455 | 2 |  |  | TEMP2_FOR_ENERGY_REC_SYSTEM | +CB.1 | 2500 FRESH WATER | 25001038_2 | Temperature Sensor 2 For Energy Recovery System | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI25 | 750-455 | 3 |  |  | ACC_SENSOR_2_OUTPX | +CB.1 | 4500 AMCS | 45019001_2 | Acceleration Sensor 2 Output X |  |  |  | 615.2W0004 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI25 | 750-455 | 4 |  |  | ACC_SENSOR_2_OUTPY | +CB.1 | 4500 AMCS |  | Acceleration Sensor 2 Output Y | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI26 | 750-455 | 1 |  |  | ACC_SENSOR_2_OUTPZ | +CB.1 | 4500 AMCS |  | Acceleration Sensor 2 Output Z | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI26 | 750-455 | 2 |  |  | PNEUMATIC_PRESSURE | +CB.1 | 2900 PNEUMATIC | 29001019 | Pressure |  |  |  | 425W0003 | [12 empty] | 0 | 16 | Bar |  | 215 |  |  | 6 |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Float | KEB1 | AI26 | 750-455 | 3 |  |  | LEVEL_GREY_WATER_TANK_AFT_SB | +CB.1 | 3400 SEWAGE | 34001025_1 | Level Sensor Grey Water Tank Aft FR 53 SB |  |  |  | 447W0019 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI26 | 750-455 | 4 |  |  | LEVEL_GREY_WATER_TANK_AFT_SB | +CB.1 | 3400 SEWAGE | 34001025_2 | Level Sensor Black & Grey Water Tank FR 48 PS |  |  |  | 447W0020 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI27 | 750-455 | 1 |  |  | LEVEL_SLUDGE_TANK | +CB.1 | 3400 SEWAGE | 34001025_3 | Level Sensor Sludge Tank FR 50 |  |  |  | 447W0021 | [14 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI27 | 750-455 | 2 |  |  | MAIN_DECKH_VENT_HATCH_SB_PERC | +CB.1 | 0900 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch SB Nr.33 Percentage Open |  |  |  | 535W0020 | [12 empty] | 0 | 100 | %
R1.10 |  | Float | KEB1 | AI27 | 750-455 | 3 |  |  | MAIN_DECKH_VENT_HATCH_PS_PERC | +CB.1 | 0900 DOORS HATCHES |  | Main Deckhouse Ventilation Hatch PS Nr.34 Percentage Open |  |  |  | 535W0022 | [12 empty] | 0 | 100 | %
R1.10 |  | Float | KEB1 | AI27 | 750-455 | 4 |  |  | AFT_DECKH_VENT_HATCH_PERC | +CB.1 | 0900 DOORS HATCHES |  | Aft Deckhouse Ventilation Hatch Nr.44 Percentage Open |  |  |  | 535W0042 | [12 empty] | 0 | 100 | %
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 1 |  |  | TECH_WAT_SALINITY | +CB.1 | 2500 TECHWATER |  | Salinity Sensor | [18 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 2 |  |  | TECH_WAT_TANK1_LEVEL | +CB.1 | 2500 TECHWATER | 25004025_1 | Level Sensor Technical Water Tank1 FR tbd SB |  |  |  | 421.2W0030 | 2x2x0.75 | [11 empty] | 0 | 100 | % |  | 223 | 90 | 80 |  |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 3 |  |  | TECH_WAT_TANK2_LEVEL | +CB.1 | 2500 TECHWATER | 25001025_2 | Level Sensor Technical Water Tank2 FR45 SB |  |  |  | 421.2W0031 | 2x2x0.75 | [11 empty] | 0 | 100 | % |  | 224 | 90 | 80 |  |  |  | 3 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Float | KEB1 | AI28 | 750-455 | 4 |  |  | TECH_WAT_FLOW_CHARCOAL_FILTER_B01 | +CB.1 | 2500 TECHWATER | 25004037_4 | Flow Sensor Charcoal Filter B01 |  |  |  | 421.2W0032 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI29 | 750-455 | 1 |  |  | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B04 | +CB.1 | 2500 TECHWATER | 25004037_3 | Flow Sensor Reel For Deckwash B04 |  |  |  | 421.2W0033 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI29 | 750-455 | 2 |  |  | TECH_WAT_FLOW_CHARCOAL_FILTER_B02 | +CB.1 | 2500 TECHWATER | 25004038 | Flow Sensor Charcoal Filter B02 |  |  |  | 421.2W0041 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI29 | 750-455 | 3 |  |  | TECH_WAT_FLOW_ADIABATIC_COOL_B03 | +CB.1 | 2500 TECHWATER | 25004034_1 | Flow Sensor Adiabatic Cooling Line B03 |  |  |  | 421.2W0042 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI29 | 750-455 | 4 |  |  | TECH_WAT_FLOW_ADIABATIC_COOL_B07 | +CB.1 | 2500 TECHWATER | 25004034_2 | Flow Sensor Adiabatic Cooling Line B07 |  |  |  | 421.2W0043 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI30 | 750-455 | 1 |  |  | TECH_WAT_FLOW_ADIABATIC_COOL_B08 | +CB.1 | 2500 TECHWATER | 25004034_3 | Flow Sensor Adiabatic Cooling Line B08 |  |  |  | 421.2W0044 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB1 | AI30 | 750-455 | 2 |  |  | TECH_WAT_FLOW_ADIABATIC_COOL_B09 | +CB.1 | 2500 TECHWATER | 25004034_4 | Flow Sensor Adiabatic Cooling Line B09 |  |  |  | 421.2W0045 | 2x2x0.75 | [13 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI30 | 750-455 | 3 |  |  | Spare_AI30_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI30 | 750-455 | 4 |  |  | Spare_AI30_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.8 |  | Float | KEB1 | AI31 | 750-450 | 1 |  |  | STERN_THRUST_BEARING_TEMP_DE | +CB.1 | 1500 PROPULSION |  | Stern Thrust Motor Bearing Temperature DE | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI31 | 750-450 | 2 |  |  | STERN_THRUST_BEARING_TEMP_NDE | +CB.1 | 1500 PROPULSION |  | Stern Thrust Motor Bearing Temperature NDE | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI31 | 750-450 | 3 |  |  | Spare_AI31_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI31 | 750-450 | 4 |  |  | Spare_AI31_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI32 | 750-450 | 1 |  |  | Spare_AI32_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI32 | 750-450 | 2 |  |  | Spare_AI32_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI32 | 750-450 | 3 |  |  | Spare_AI32_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI32 | 750-450 | 4 |  |  | Spare_AI32_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI33 | 750-450 | 1 |  |  | Spare_AI33_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI33 | 750-450 | 2 |  |  | Spare_AI33_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI33 | 750-450 | 3 |  |  | Spare_AI33_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI33 | 750-450 | 4 |  |  | Spare_AI33_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI34 | 750-450 | 1 |  |  | Spare_AI34_1_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI34 | 750-450 | 2 |  |  | Spare_AI34_2_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI34 | 750-450 | 3 |  |  | Spare_AI34_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB1 | AI34 | 750-450 | 4 |  |  | Spare_AI34_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1 | [18 empty] | 4-20mA
R1.9 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __1 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __2 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __3 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __4 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __5 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __6 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __7 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __8 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __9 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __10 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __11 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __12 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __13 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __14 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __15 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __16 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __17 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __18 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __19 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __20 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __21 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __22 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __23 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __24 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __25 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __26 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __27 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __28 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __29 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __30 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __31 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __32 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __33 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __34 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __35 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __36 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __37 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __38 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __39 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __40 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __41 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __42 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __43 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __44 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __45 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __46 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __47 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __48 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __49 | [18 empty] | 4-20mA
R1.8 | True | Int16 | KEB1 | SE1_DMX | 750-652 |  |  |  | Spare_SE1_DMX__ | +CB.1 | SPARE |  | Spare Yard __50 | [18 empty] | 4-20mA
R1.8 |  | Bool | KEB1 | F2 | 750-610 | 1 |  |  | AmcsPlcPowerModule2FuseBlown | +CB.1 | 4500 AMCS |  | AMCS PLC KEB1 Power Module 2 Fuse Blown | [20 empty] | 300 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB1 | F2 | 750-610 | 2 |  |  | AmcsPlcPowerModule2PowerFailure | +CB.1 | 4500 AMCS |  | AMCS PLC KEB1 Power Module 2 Power Failure | [20 empty] | 301 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1,10 |  | Bool | KEB1 | AO60 | 750-555 | 1 |  |  | BATT_VENT_AFT_PS_SPEED | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT PS Speed |  |  |  | 412.3W0003 | [12 empty] | 0 | 100 | %
R1,10 |  | Bool | KEB1 | AO60 | 750-555 | 2 |  |  | BATT_VENT_AFT_SB_SPEED | +CB.1 | 3500 VENTILATION |  | Battery Ventilation AFT SB Speed |  |  |  | 412.3W0006 | [12 empty] | 0 | 100 | %
R1,10 |  | Bool | KEB1 | AO60 | 750-555 | 3 |  |  | Spare_AO60_3_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | AO60 | 750-555 | 4 |  |  | Spare_AO60_4_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R0.1 |  | Bool | KEB1 | DO60 | 750-1500 | 1 |  |  | GEN_SERV_PUMP2_FIELD_RUNN_FDBCK | +CB.1 | 2100 GENERAL SERVICE | 21001004 | General Service Pump 2 Field Running Feedback |  |  |  | 381W0003
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 2 |  |  | STRIP_PUMP_START | +CB.1 | 2100 BILGE FIFI | 21001004 | Stripping Pump Start Command |  |  |  | 381W0010
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 3 |  |  | STRIP_PUMP_STOP | +CB.1 | 2100 BILGE FIFI |  | Stripping Pump Stop Command
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 4 |  |  | CHAIN_LOCK_PUMP_START | +CB.1 | 2100 BILGE FIFI | 21001005 | Chain Locker Pump Start Command
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 5 |  |  | CHAIN_LOCK_PUMP_STOP | +CB.1 | 2100 BILGE FIFI |  | Chain Locker Pump Stop Command
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 6 |  |  | SUBMERS_PUMP1_LEVEL_HIGH | +CB.1 | 2100 BILGE FIFI | 21001006-1 | Submersible Pump 1 Level High (Start) |  |  |  | 381W0009
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 7 |  |  | SUBMERS_PUMP2_LEVEL_HIGH | +CB.1 | 2100 BILGE FIFI | 21001006-2 | Submersible Pump 2 Level High (Start) |  |  |  | 381W0085
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 8 |  |  | SUBMERS_PUMP3_LEVEL_HIGH | +CB.1 | 2100 BILGE FIFI | 21001006-3 | Submersible Pump 3 Level High (Start) |  |  |  | 381W0009
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 9 |  |  | SEPARATOR_START | +CB.1 | 2100 BILGE FIFI | 21001007 | Bilge Separator Start |  |  |  | 381W0009
R1.0 |  | Bool | KEB1 | DO60 | 750-1500 | 10 |  |  | GEN_SERV_PUMP2_FIELD_AVAIL_FDBCK | +CB.1 | 2100 GENERAL SERVICE |  | General Service Pump 2 Field Available Feedback
R1.3 |  | Bool | KEB1 | DO60 | 750-1500 | 11 |  |  | GEN_SERV_PUMP2_FIELD_FAULT_FDBCK | +CB.1 | 2100 GENERAL SERVICE |  | General Service Pump 2 Field Fault Feedback
R1.3 |  | Bool | KEB1 | DO60 | 750-1500 | 12 |  |  | ACTIVATE_HULL_TEMP_MEASUREMENT | +CB.1 | AMCS - CTRL |  | Activate Hull Temperature measurement
R1.5 |  | Bool | KEB1 | DO60 | 750-1500 | 13 |  |  | TRANS_PUMP_BLCK_WAT_START_STOP | +CB.1 | 3400 SEWAGE | 34001001 | Transfer Pump 2 Black Water Start/Stop |  |  |  | 447W0003
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 14 |  |  | TRANS_PUMP_GREY_WAT_START_STOP | +CB.1 | 3400 SEWAGE | 34001002 | Transfer Pump 1 Grey Water Start/Stop |  |  |  | 447W0007
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 15 |  |  | PUMP_FWD_GRAY_WAT_START_STOP | +CB.1 | 3400 SEWAGE | 34001003 | Pump 3 Fwd Gray Water Start/Stop |  |  |  | 447W0003
R1.7 |  | Bool | KEB1 | DO60 | 750-1500 | 16 |  |  | VENT_SUPP_TECH_SPACE_START_STOP | +CB.1 | 3500 VENTILATION |  | Ventilation Supply Technical Space Start/Stop
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 1 |  |  | VENT_EXTR_TECH_SPACE_START_STOP | +CB.1 | 3500 VENTILATION |  | Ventilation Extractor Technical Space Start/Stop
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 2 |  |  | VENT_FP_FR10_PS_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-1 | Ventilation Forepeak FR10 PS On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 3 |  |  | VENT_FP_FR10_PS_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-1 | Ventilation Forepeak FR10 PS Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 4 |  |  | VENT_LOCK_FR19_PS_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-2 | Ventilation Locker FR19 PS On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 5 |  |  | VENT_LOCK_FR19_PS_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-2 | Ventilation Locker FR19 PS Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 6 |  |  | VENT_LOCK_FR27_PS_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-3 | Ventilation Locker FR27 PS On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 7 |  |  | VENT_LOCK_FR27_PS_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-3 | Ventilation Locker FR27 PS Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 8 |  |  | VENT_LOCK_FR27_SB_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-4 | Ventilation Locker FR27 SB On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 9 |  |  | VENT_LOCK_FR27_SB_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-4 | Ventilation Locker FR27 SB Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 10 |  |  | VENT_LOCK_FR40_PS_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-5 | Ventilation Locker FR40 PS On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 11 |  |  | VENT_LOCK_FR40_PS_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-5 | Ventilation Locker FR40 PS Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 12 |  |  | VENT_LOCK_FR40_SB_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-6 | Ventilation Locker FR40 SB On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 13 |  |  | VENT_LOCK_FR40_SB_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-6 | Ventilation Locker FR40 SB Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 14 |  |  | VENT_LOCK_FR48_PS_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-7 | Ventilation Locker FR48 PS On/Off
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 15 |  |  | VENT_FLOCK_R48_PS_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-7 | Ventilation FLocker R48 PS Speed Low/High
R1.10 |  | Bool | KEB1 | DO61 | 750-1500 | 16 |  |  | VENT_LAZ_FR73_PS_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-8 | Ventilation Lazarette FR73 PS On/Off
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 1 |  |  | VENT_LAZ_FR73_PS_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-8 | Ventilation Lazarette FR73 PS Speed Low/High
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 2 |  |  | VENT_LAZ_FR73_SB_ON_OFF | +CB.1 | 3500 VENTILATION | 35002266-9 | Ventilation Lazarette FR73 SB On/Off
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 3 |  |  | VENT_LAZ_FR73_SB_SPEED_LOW_HIGH | +CB.1 | 3500 VENTILATION | 35002266-9 | Ventilation Lazarette FR73 SB Speed Low/High
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 4 |  |  | TECH_WAT_VALVE_COLD_AIR_FR68_Y03_OPEN_CLOSE | +CB.1 | 2500 TECHWATER | 25004020_1 | Valve For Cold Air Cooling Water FR68 Y03
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 5 |  |  | TECH_WAT_VALVE_COLD_AIR_FR32_Y04_OPEN_CLOSE | +CB.1 | 2500 TECHWATER | 25004020_2 | Valve For Cold Air Cooling Water FR32 Y04
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 6 |  |  | TECH_WAT_VALVE_COLD_AIR_FR32_Y05_OPEN_CLOSE | +CB.1 | 2500 TECHWATER | 25004020_3 | Valve For Cold Air Cooling Water FR32 Y05
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 7 |  |  | Spare_DO62_7_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 8 |  |  | Spare_DO62_8_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 9 |  |  | Spare_DO62_9_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 10 |  |  | Spare_DO62_10_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 11 |  |  | Spare_DO62_11_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 12 |  |  | Spare_DO62_12_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 13 |  |  | Spare_DO62_13_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 14 |  |  | Spare_DO62_14_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 15 |  |  | Spare_DO62_15_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
R1.10 |  | Bool | KEB1 | DO62 | 750-1500 | 16 |  |  | Spare_DO62_16_ | +CB.1 | SPARE |  | Spare Yard __+CB.1
| True | [11 empty] | Serial Interface - KEC1 Port1
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var1 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var2 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var3 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var4 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var5 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var6 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var7 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var8 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var9 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var10 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var11 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var12 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var13 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var14 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var15 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var16 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var17 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var18 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var19 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var20 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var21 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var22 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var23 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var24 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var25 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var26 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var27 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var28 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var29 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var30 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var31 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var32 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var33 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var34 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var35 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var36 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var37 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var38 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var39 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var40 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var41 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var42 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var43 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var44 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var45 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var46 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var47 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var48 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var49 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P1 | [5 empty] | Serial__Var50 | +CB.1 | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC1 Port2
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var1 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var2 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var3 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var4 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var5 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var6 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var7 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var8 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var9 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var10 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var11 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var12 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var13 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var14 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var15 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var16 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var17 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var18 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var19 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var20 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var21 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var22 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var23 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var24 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var25 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var26 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var27 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var28 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var29 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var30 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var31 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var32 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var33 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var34 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var35 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var36 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var37 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var38 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var39 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var40 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var41 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var42 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var43 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var44 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var45 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var46 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var47 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var48 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var49 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P2 | [5 empty] | Serial__Var50 | +CB.1 | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC1 Port3
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var1 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var2 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var3 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var4 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var5 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var6 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var7 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var8 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var9 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var10 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var11 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var12 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var13 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var14 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var15 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var16 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var17 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var18 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var19 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var20 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var21 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var22 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var23 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var24 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var25 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var26 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var27 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var28 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var29 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var30 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var31 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var32 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var33 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var34 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var35 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var36 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var37 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var38 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var39 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var40 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var41 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var42 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var43 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var44 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var45 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var46 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var47 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var48 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var49 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P3 | [5 empty] | Serial__Var50 | +CB.1 | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC1 Port4
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var1 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var2 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var3 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var4 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var5 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var6 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var7 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var8 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var9 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var10 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var11 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var12 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var13 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var14 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var15 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var16 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var17 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var18 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var19 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var20 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var21 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var22 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var23 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var24 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var25 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var26 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var27 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var28 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var29 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var30 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var31 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var32 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var33 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var34 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var35 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var36 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var37 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var38 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var39 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var40 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var41 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var42 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var43 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var44 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var45 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var46 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var47 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var48 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var49 | +CB.1 | SPARE |  | TODO
R1.8 | True |  | KEC1_P4 | [5 empty] | Serial__Var50 | +CB.1 | SPARE |  | TODO
| True | [11 empty] | ALARM CABINET - AMCS Crew Mess +CB.2
R1.8 |  | Bool | KEB2 | DI00 | 750-1415 | 1 |  |  | AmcsPowerSupplyFailure | +CB.2 | 4500 AMCS |  | CREW MESS AMCS Power Supply Failure | [20 empty] | 559 |  |  |  |  | False |  | TS |  | Alarm | Check Primary (G2) supply, Secundary (G3) supply and redundancy module (G1) |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI00 | 750-1415 | 2 |  |  | Spare_DI00_2 | +CB.2 | 4500 AMCS |  | Spare | [20 empty] | 560 |  |  |  |  | False |  | TS |  | Alarm | Check for earth fault |  |  |  |  | 1
R1.9 |  | Bool | KEB2 | DI00 | 750-1415 | 3 |  |  | Spare_DI00_3 | +CB.2 | 4500 AMCS |  | Spare
R1.9 |  | Bool | KEB2 | DI00 | 750-1415 | 4 |  |  | Spare_DI00_4 | +CB.2 | 4500 AMCS |  | Spare
R0.4 |  | Bool | KEB2 | DI00 | 750-1415 | 5 |  |  | BridgeBuzzersPowerSupplyFailure | +CB.2 | 4500 AMCS |  | Bridge Buzzers Power Supply Failure
R0.4 |  | Bool | KEB2 | DI00 | 750-1415 | 6 |  |  | BridgeAlarmPanelSilenceButton | +CB.2 | 4500 AMCS |  | Bridge Alarm Panel Silence Button
R1.4 |  | Bool | KEB2 | DI00 | 750-1415 | 7 |  |  | OperatorBuzzersPowerSupplyFailure | +CB.2 | 4500 AMCS |  | Operator Buzzers Power Supply Failure
R1.4 |  | Bool | KEB2 | DI00 | 750-1415 | 8 |  |  | OperatorAlarmPanelSilenceButton | +CB.2 | 4500 AMCS |  | Operator Alarm Panel Silence Button
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 1 |  |  | UmsCabin1Silence | +CB.2 | 4500 AMCS |  | UMS Cabin 1 Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 2 |  |  | UmsCabin2Silence | +CB.2 | 4500 AMCS |  | UMS Cabin 2 Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 3 |  |  | UmsCabin3Silence | +CB.2 | 4500 AMCS |  | UMS Cabin 3 Silence
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 4 |  |  | Spare_DI01_4 | +CB.2 | 4500 AMCS |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 5 |  |  | Spare_DI01_5 | +CB.2 | 4500 AMCS |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 6 |  |  | Spare_DI01_6 | +CB.2 | 4500 AMCS |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 7 |  |  | Spare_DI01_7 | +CB.2 | 4500 AMCS |  | Spare
R1.0 |  | Bool | KEB2 | DI01 | 750-1415 | 8 |  |  | Spare_DI01_8 | +CB.2 | 4500 AMCS |  | Spare
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 1 |  |  | UmsCabin1Buzzer | +CB.2 | 4500 AMCS |  | UMS Cabin 1 Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 2 |  |  | UmsCabin2Buzzer | +CB.2 | 4500 AMCS |  | UMS Cabin 2 Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 3 |  |  | UmsCabin3Buzzer | +CB.2 | 4500 AMCS |  | UMS Cabin 3 Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 4 |  |  | BridgeAlarmPanelSilenceLight | +CB.2 | 4500 AMCS |  | Bridge Alarm Panel Silence Light
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 5 |  |  | OperatorAlarmPanelSilenceLight | +CB.2 | 4500 AMCS |  | Operator Alarm Panel Silence Light
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 6 |  |  | MachinerySpaceBuzzerHorn | +CB.2 | 4500 AMCS |  | Machinery Space Buzzer Horn
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 7 |  |  | BridgeAlarmPanelBuzzer | +CB.2 | 4500 AMCS |  | Bridge Alarm Panel Buzzer
R1.6 |  | Bool | KEB2 | DO00 | 750-1515 | 8 |  |  | OperatorAlarmPanelBuzzer | +CB.2 | 4500 AMCS |  | Operator Alarm Panel Buzzer
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 1 |  |  | UMSCabin1Duty | +CB.2 | 4500 AMCS |  | UMS Cabin 1 Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 2 |  |  | UMSCabin1AlarmLed | +CB.2 | 4500 AMCS |  | UMS Cabin 1 Alarm Led
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 3 |  |  | UMSCabin2Duty | +CB.2 | 4500 AMCS |  | UMS Cabin 2 Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 4 |  |  | UMSCabin2AlarmLed | +CB.2 | 4500 AMCS |  | UMS Cabin 2 Alarm Led
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 5 |  |  | UMSCabin3Duty | +CB.2 | 4500 AMCS |  | UMS Cabin 3 Duty
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 6 |  |  | UMSCabin3AlarmLed | +CB.2 | 4500 AMCS |  | UMS Cabin 3 Alarm Led
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 7 |  |  | Spare_DO01_7 | +CB.2 | 4500 AMCS |  | Spare
R1.6 |  | Bool | KEB2 | DO01 | 750-1515 | 8 |  |  | Spare_DO01_8 | +CB.2 | 4500 AMCS |  | Spare
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 1 |  |  | AmcsPlcPowerModule1InternalFuseBlown | +CB.2 | 4500 AMCS |  | AMCS PLC KEB2 Power Module 2 Internal Fuse Blown | [20 empty] | 591 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 2 |  |  | AmcsPlcPowerModule1PowerFailure | +CB.2 | 4500 AMCS |  | AMCS PLC KEB2 Power Module 2 Power Failure | [20 empty] | 592 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 1 |  |  | BILGE_FRAME68_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-1 | Water Sensor in Hull Fr.68 Alarm |  |  |  | 381W0024 | [16 empty] | 593 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 2 |  |  | BILGE_FRAME53_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-2 | Water Sensor in Hull Fr.53 Alarm |  |  |  | 381W0025 | [16 empty] | 594 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 3 |  |  | BILGE_FRAME48_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-3 | Water Sensor in Hull Fr.48 Alarm |  |  |  | 381W0026 | [16 empty] | 595 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 4 |  |  | BILGE_FRAME46_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-4 | Water Sensor in Hull Fr.46 Alarm |  |  |  | 381W0027 | [16 empty] | 596 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 5 |  |  | BILGE_FRAME38_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-5 | Water Sensor in Hull Fr.38 Alarm |  |  |  | 381W0037 | [16 empty] | 597 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 6 |  |  | BILGE_FRAME30_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-6 | Water Sensor in Hull Fr.30 Alarm |  |  |  | 381W0038 | [16 empty] | 598 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 7 |  |  | BILGE_FRAME15_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-7 | Water Sensor in Hull Fr.15 Alarm |  |  |  | 381W0029 | [16 empty] | 599 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI20 | 750-1415 | 8 |  |  | BILGE_FRAME13_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-8 | Water Sensor in Hull Fr.13 Alarm |  |  |  | 381W0036 | [16 empty] | 600 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 1 |  |  | BILGE_FRAME47SB_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-9 | Water Sensor in Hull Fr.47 SB Alarm |  |  |  | 381W0028 | [16 empty] | 601 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 2 |  |  | BILGE_FRAME54PS_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-10 | Water Sensor in Hull Fr.54 PS Alarm |  |  |  | 381W0050 | [16 empty] | 602 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 3 |  |  | BILGE_FRAME54SB_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-11 | Water Sensor in Hull Fr.54 SB Alarm |  |  |  | 381W0051 | [16 empty] | 603 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 4 |  |  | BILGE_FRAME38PS_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-12 | Water Sensor in Hull Fr.38 PS Alarm |  |  |  | 381W0057 | [16 empty] | 604 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 5 |  |  | BILGE_FRAME38SB_ALARM | +CB.2 | 2100 BILGE FIFI | 21001031-13 | Water Sensor in Hull Fr.38 SB Alarm |  |  |  | 381W0058 | [16 empty] | 605 |  |  |  |  | False | 5 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI21 | 750-1415 | 6 |  |  | BCKUP_GEN_SERV_PUMP_REM_AVAIL | +CB.2 | 2100 GENERAL SERVICE | 21001003 | Backup General Service Pump Remote Available |  |  |  | 381W0008
R1.1 |  | Bool | KEB2 | DI21 | 750-1415 | 7 |  |  | BCKUP_GEN_SERV_PUMP_FIELD_START | +CB.2 | 2100 GENERAL SERVICE |  | Backup General Service Pump Field Start
R1.1 |  | Bool | KEB2 | DI21 | 750-1415 | 8 |  |  | BCKUP_GEN_SERV_PUMP_FIELD_STOP | +CB.2 | 2100 GENERAL SERVICE |  | Backup General Service Pump Field Stop
R1.1 |  | Bool | KEB2 | DI22 | 750-1415 | 1 |  |  | MON_SCROLL_INPUT_PS_HELMSTATION | +CB.2 | 4500 AMCS |  | Monitor Scroll Input PS Helmstation |  |  |  | 58A-C37 | CAT7
R1.2 |  | Bool | KEB2 | DI22 | 750-1415 | 2 |  |  | MON_SCROLL_INPUT_SB_HELMSTATION | +CB.2 | 4500 AMCS |  | Monitor Scroll Input SB Helmstation |  |  |  | 58A-C72 | CAT7
R1.2 |  | Bool | KEB2 | DI22 | 750-1415 | 3 |  |  | MON_SCROLL_INPUT_SHIPS_OFFICE | +CB.2 | 4500 AMCS |  | Monitor Scroll Input Ships Office |  |  |  | 58A-C49 | CAT7
R0.1 |  | Bool | KEB2 | DI22 | 750-1415 | 4 |  |  | MON_SCROLL_INPUT_CREW_MESS | +CB.2 | 4500 AMCS |  | Monitor Scroll Input Crew Mess |  |  |  | 58A-C26 | CAT7
R0.1 |  | Bool | KEB2 | DI22 | 750-1415 | 5 |  |  | MON_SCROLL_INPUT_CAPTAINS_CABIN | +CB.2 | 4500 AMCS |  | Monitor Scroll Input Captains Cabin |  |  |  | 58A-C60 | CAT7
R0.1 |  | Bool | KEB2 | DI22 | 750-1415 | 6 |  |  | DECK_CRANE_GEN_ALARM | +CB.2 | 7500 DECK CRANE | 22AJB7/10.0 | General Alarm |  |  |  | 511W0002 | [16 empty] | 614 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | DI22 | 750-1415 | 7 |  |  | MOB_TENDER_HATCH_CL_LOCK | +CB.2 | 7500 DECK CRANE | 22AJB7/10.1 | MOB Tender Hatch Closed & Locked
R1.7 |  | Bool | KEB2 | DI22 | 750-1415 | 8 |  |  | GUEST_TENDER_HATCH_CL_LOCK | +CB.2 | 7500 DECK CRANE | 22AJB7/10.2 | Guest Tender Hatch Closed & Locked
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 1 |  |  | SAIL_STOR_HATCH | +CB.2 | 0900 DOORS HATCHES |  | Sail Storage Hatch Nr.2 |  |  |  | 535W0006
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 2 |  |  | FOREPEAK_ACC_HATCH | +CB.2 | 0900 DOORS HATCHES |  | Forepeak Access Hatch Nr.3 |  |  |  | 535W0007
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 3 |  |  | DINGHY_STOR_ACC_FWD | +CB.2 | 0900 DOORS HATCHES |  | Dinghy Storage Access Fwd Nr.7A |  |  |  | 535W0008
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 4 |  |  | CRANE__HATCH_AFT | +CB.2 | 0900 DOORS HATCHES |  | Crane Hatch Aft Nr.7D |  |  |  | 535W0009
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 5 |  |  | FORESHIP_STOR_AREA_ACC_HATCH | +CB.2 | 0900 DOORS HATCHES |  | Foreship Storage Area Access Hatch Nr.9 |  |  |  | 535W0010
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 6 |  |  | CREW_ESCAPE_HATCH | +CB.2 | 0900 DOORS HATCHES |  | Crew Escape Hatch Nr.15 |  |  |  | 535W0012
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 7 |  |  | CREW_AREA_ACC_DOOR | +CB.2 | 0900 DOORS HATCHES |  | Crew Area Access Door Nr.19 |  |  |  | 535W0014
R1.7 |  | Bool | KEB2 | DI23 | 750-1415 | 8 |  |  | FIRE_DETECT_FAULT | +CB.2 | 4500 FIREDETECTION |  | System Fault |  |  |  | 201W0502 | 4x2x0.75 | [15 empty] | 624 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 1 |  |  | BCKUP_GEN_SERV_PUMP_START_RUN | +CB.2 | 2100 GENERAL SERVICE | 21001003 | Backup General Service Pump Start / Running
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 2 |  |  | BATT_VENT_FWD_PS_ON_RUN | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD PS On / Run |  |  |  | 412.3W0010
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 3 |  |  | BATT_VENT_FWD_PS_ON_FAULT | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD PS Fault | [20 empty] | 627 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 4 |  |  | BATT_VENT_FWD_PS_ON_READY | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD PS Ready
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 5 |  |  | BATT_VENT_FWD_SB_ON_RUN | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD SB On / Run |  |  |  | 412.3W0011
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 6 |  |  | BATT_VENT_FWD_SB_ON_FAULT | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD SB Fault | [20 empty] | 630 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 7 |  |  | BATT_VENT_FWD_SB_ON_READY | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD SB Ready
R1.10 |  | Bool | KEB2 | DI24 | 750-1415 | 8 |  |  | WTID_TECH_ROOM_ACCESS_DOOR | +CB.2 | 0900 DOORS HATCHES |  | WTID Technical Room Access Door |  |  |  | 531.1W0004 | 2x2x0.75
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 1 |  |  | WTID_FWD_CORRIDOR_DOOR | +CB.2 | 0900 DOORS HATCHES |  | WTID Fwd End Corridor Door |  |  |  | 531.1W0005 | 2x2x0.75
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 2 |  |  | WTID_AFT_CORRIDOR_DOOR | +CB.2 | 0900 DOORS HATCHES |  | WTID Aft End corridor Door |  |  |  | 531.1W0006 | 2x2x0.75
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 3 |  |  | WTSD_CLOSE_DOOR | +CB.2 | 0900 DOORS HATCHES |  | WTSD Close Door | [25 empty] | False
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 4 |  |  | WTSD_MAIN_BACKUP_PWR_FAIL | +CB.2 | 0900 DOORS HATCHES |  | WTSD Man/Backup Power Failure
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 5 |  |  | Spare_DI25_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 6 |  |  | WTSD_DOOR_OPENED | +CB.2 | 0900 DOORS HATCHES |  | WTSD Door Opened
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 7 |  |  | WTSD_DOOR_CLOSED | +CB.2 | 0900 DOORS HATCHES |  | WTSD Door Closed
R1.10 |  | Bool | KEB2 | DI25 | 750-1415 | 8 |  |  | WTSD_LOW_AIR_PRESS | +CB.2 | 0900 DOORS HATCHES |  | WTSD Low Air Pressure
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 1 |  |  | STEER_OIL_LEVEL_TOO_LOW | +CB.2 | xxxx STEERING STYSTEM |  | Oil Level Too Low |  |  |  | 311W0011 | [16 empty] | 641 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 2 |  |  | STEER_OIL_FILTER_CLOGGED | +CB.2 | xxxx STEERING STYSTEM |  | Oil Filter Clogged | [20 empty] | 642 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 3 |  |  | STEER_24V_MONITORING | +CB.2 | xxxx STEERING STYSTEM |  | 24 Voltage Monitoring | [20 empty] | 643 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 4 |  |  | STEER_FREQ_DR_POWER_FAIL | +CB.2 | xxxx STEERING STYSTEM |  | Frequency Drive Power Failure | [20 empty] | 644 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 5 |  |  | DRAIN_VLV_Y02_POS_OVERBOARD | +CB.1 | 2500 TECHWATER | 25004014_2 | Drain water Valve Y02 Position Overboard |  |  |  | 421.2W0049 | 7x2x0,75
R1.10 |  | Bool | KEB2 | DI26 | 750-1415 | 6 |  |  | DRAIN_VLV_Y02_POS_TO_PURO | +CB.1 | 2500 TECHWATER | 25004014_2 | Drain water Valve Y02 Position to Puro
R0.1 |  | Bool | KEB2 | DI26 | 750-1415 | 7 |  |  | Spare_DI26_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI26 | 750-1415 | 8 |  |  | Spare_DI26_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 1 |  |  | Spare_DI27_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 2 |  |  | Spare_DI27_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 3 |  |  | Spare_DI27_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 4 |  |  | Spare_DI27_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 5 |  |  | Spare_DI27_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 6 |  |  | Spare_DI27_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 7 |  |  | Spare_DI27_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI27 | 750-1415 | 8 |  |  | Spare_DI27_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 1 |  |  | Spare_DI28_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 2 |  |  | Spare_DI28_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 3 |  |  | Spare_DI28_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 4 |  |  | Spare_DI28_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 5 |  |  | Spare_DI28_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 6 |  |  | Spare_DI28_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 7 |  |  | Spare_DI28_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI28 | 750-1415 | 8 |  |  | Spare_DI28_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 1 |  |  | Spare_DI29_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 2 |  |  | Spare_DI29_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 3 |  |  | Spare_DI29_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 4 |  |  | Spare_DI29_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 5 |  |  | Spare_DI29_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 6 |  |  | Spare_DI29_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 7 |  |  | Spare_DI29_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI29 | 750-1415 | 8 |  |  | Spare_DI29_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 1 |  |  | Spare_DI30_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 2 |  |  | Spare_DI30_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 3 |  |  | Spare_DI30_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 4 |  |  | Spare_DI30_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 5 |  |  | Spare_DI30_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 6 |  |  | Spare_DI30_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 7 |  |  | Spare_DI30_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI30 | 750-1415 | 8 |  |  | Spare_DI30_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 1 |  |  | Spare_DI31_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 2 |  |  | Spare_DI31_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 3 |  |  | Spare_DI31_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 4 |  |  | Spare_DI31_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 5 |  |  | Spare_DI31_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 6 |  |  | Spare_DI31_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 7 |  |  | Spare_DI31_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI31 | 750-1415 | 8 |  |  | Spare_DI31_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 1 |  |  | Spare_DI32_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 2 |  |  | Spare_DI32_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 3 |  |  | Spare_DI32_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 4 |  |  | Spare_DI32_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 5 |  |  | Spare_DI32_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 6 |  |  | Spare_DI32_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 7 |  |  | Spare_DI32_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI32 | 750-1415 | 8 |  |  | Spare_DI32_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 1 |  |  | Spare_DI33_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 2 |  |  | Spare_DI33_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 3 |  |  | Spare_DI33_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 4 |  |  | Spare_DI33_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 5 |  |  | Spare_DI33_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 6 |  |  | Spare_DI33_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 7 |  |  | Spare_DI33_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI33 | 750-1415 | 8 |  |  | Spare_DI33_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 1 |  |  | Spare_DI34_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 2 |  |  | Spare_DI34_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 3 |  |  | Spare_DI34_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 4 |  |  | Spare_DI34_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 5 |  |  | Spare_DI34_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 6 |  |  | Spare_DI34_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 7 |  |  | Spare_DI34_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI34 | 750-1415 | 8 |  |  | Spare_DI34_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 1 |  |  | Spare_DI35_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 2 |  |  | Spare_DI35_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 3 |  |  | Spare_DI35_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 4 |  |  | Spare_DI35_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 5 |  |  | Spare_DI35_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 6 |  |  | Spare_DI35_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 7 |  |  | Spare_DI35_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI35 | 750-1415 | 8 |  |  | Spare_DI35_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 1 |  |  | Spare_DI36_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 2 |  |  | Spare_DI36_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 3 |  |  | Spare_DI36_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 4 |  |  | Spare_DI36_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 5 |  |  | Spare_DI36_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 6 |  |  | Spare_DI36_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 7 |  |  | Spare_DI36_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI36 | 750-1415 | 8 |  |  | Spare_DI36_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 1 |  |  | Spare_DI37_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 2 |  |  | Spare_DI37_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 3 |  |  | Spare_DI37_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 4 |  |  | Spare_DI37_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 5 |  |  | Spare_DI37_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 6 |  |  | Spare_DI37_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 7 |  |  | Spare_DI37_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI37 | 750-1415 | 8 |  |  | Spare_DI37_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 1 |  |  | Spare_DI38_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 2 |  |  | Spare_DI38_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 3 |  |  | Spare_DI38_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 4 |  |  | Spare_DI38_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 5 |  |  | Spare_DI38_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 6 |  |  | Spare_DI38_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 7 |  |  | Spare_DI38_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI38 | 750-1415 | 8 |  |  | Spare_DI38_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 1 |  |  | Spare_DI39_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 2 |  |  | Spare_DI39_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 3 |  |  | Spare_DI39_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 4 |  |  | Spare_DI39_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 5 |  |  | Spare_DI39_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 6 |  |  | Spare_DI39_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 7 |  |  | Spare_DI39_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DI39 | 750-1415 | 8 |  |  | Spare_DI39_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Float | KEB2 | AI20 | 750-455 | 1 |  |  | CHAIN_LOCK_PRESS_SENSOR | +CB.2 | 2100 BILGE FIFI | 21001049-1 | Chain Locker Bilge Level |  |  |  | 381W0048 | [12 empty] | 0 | xx | bar |  | 753 |  | xx |  |  |  | 20 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 2 |  |  | BILGE_TANK_PRESS_SENSOR | +CB.2 | 2101 BILGE FIFI | 21001050 | Bilge Tank Level |  |  |  | 381W0049 | [12 empty] | 0 | xx | bar |  | 754 |  | xx |  |  |  | 20 | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 3 |  |  | FLOW_CREW_MESS_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_18 | Flow Sensor Crew Mess Hot Water |  |  |  | 421.1W0106 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI20 | 750-455 | 4 |  |  | FLOW_CREW_MESS_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_17 | Flow Sensor Crew Mess Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 1 |  |  | FLOW_GALLEY_1_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_20 | Flow Sensor Galley 1 Hot Water |  |  |  | 421.1W0107 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 2 |  |  | FLOW_GALLEY_1_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_19 | Flow Sensor Galley 1 Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 3 |  |  | FLOW_GALLEY_2_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_22 | Flow Sensor Galley 2 Hot Water |  |  |  | 421.1W0108 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI21 | 750-455 | 4 |  |  | FLOW_GALLEY_2_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_21 | Flow Sensor Galley 2 Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 1 |  |  | FLOW_OVERFL_CABIN_BATHR_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_23 | Flow Sensor Overflow Cabin Bathroom Cold Water |  |  |  | 421.1W0109 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 2 |  |  | FLOW_GUEST_BATHR_PS_FWD_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_25 | Flow Sensor Guest Cabin Bathroom PS Fwd Hot Water |  |  |  | 421.1W0110 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 3 |  |  | FLOW_GUEST_BATHR_PS_FWD_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_24 | Flow Sensor Guest Cabin Bathroom PS Fwd Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI22 | 750-455 | 4 |  |  | FLOW_LAUNDRY_PS_1_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_15 | Flow Sensor Laundry PS 1 Hot Water |  |  |  | 421.1W0111 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 1 |  |  | FLOW_LAUNDRY_PS_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_14 | Flow Sensor Laundry PS Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 2 |  |  | FLOW_LAUNDRY_PS_2_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_16 | Flow Sensor Laundry PS 2 Hot Water |  |  |  | 421.1W0112 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 3 |  |  | FLOW_CAPTAINS_CABIN_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_13 | Flow Sensor Captains Cabin Hot Water |  |  |  | 421.1W0113 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI23 | 750-455 | 4 |  |  | FLOW_CAPTAINS_CABIN_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_12 | Flow Sensor Captains Cabin Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI24 | 750-455 | 1 |  |  | FLOW_CREW_CABIN_SB_AFT_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_10 | Flow Sensor Crew Cabin SB Aft Hot Water |  |  |  | 421.1W0126 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI24 | 750-455 | 2 |  |  | FLOW_CREW_CABIN_SB_AFT_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_11 | Flow Sensor Crew Cabin SB Aft Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI24 | 750-455 | 3 |  |  | FLOW_CREW_CABIN_SB_MID_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_9 | Flow Sensor Crew Cabin SB Mid Hot Water |  |  |  | 421.1W0127 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI24 | 750-455 | 4 |  |  | FLOW_CREW_CABIN_SB_MID_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_8 | Flow Sensor Crew Cabin SB Mid Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI25 | 750-455 | 1 |  |  | FLOW_CREW_CABIN_PS_MID_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_7 | Flow Sensor Crew Cabin PS Mid Hot Water |  |  |  | 421.1W0128 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI25 | 750-455 | 2 |  |  | FLOW_CREW_CABIN_PS_MID_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_6 | Flow Sensor Crew Cabin PS Mid Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI25 | 750-455 | 3 |  |  | FLOW_CREW_CABIN_SB_FWD_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_5 | Flow Sensor Crew Cabin SB Fwd Hot Water |  |  |  | 421.1W0129 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI25 | 750-455 | 4 |  |  | FLOW_CREW_CABIN_SB_FWD_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_4 | Flow Sensor Crew Cabin SB Fwd Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI26 | 750-455 | 1 |  |  | FLOW_CREW_CABIN_PS_FWD_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_3 | Flow Sensor Crew Cabin PS Fwd Hot Water |  |  |  | 421.1W0130 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI26 | 750-455 | 2 |  |  | FLOW_CREW_CABIN_PS_FWD_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_2 | Flow Sensor Crew Cabin PS Fwd Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI26 | 750-455 | 3 |  |  | FLOW_DECKHOUSE_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_28 | Flow Sensor Deckhouse Hot Water |  |  |  | 421.1W0131 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI26 | 750-455 | 4 |  |  | FLOW_DECKHOUSE_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_26 | Flow Sensor Deckhouse Cold Water | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI27 | 750-455 | 1 |  |  | FLOW_DECK_FR48_SB_TECH_COR_HOT_WATER | +CB.2 | 2500 FRESH WATER | 25001037_29 | Flow Sensor Deck Douche FR48 SB Technical Corridor Hot Water |  |  |  | 421.1W0144 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI27 | 750-455 | 2 |  |  | FLOW_DECK_FR48_SB_TECH_COR_COLD_WATER | +CB.2 | 2500 FRESH WATER | 25001037_27 | Flow Sensor Deck Douche FR48 SB Technical Corridor Cold Water |  |  |  | 421.1W0145 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI27 | 750-455 | 3 |  |  | PRESS_FR_46_SYSTEM_BEH_PRES_PUMPS | +CB.2 | 2500 FRESH WATER | 25001036 | Pressure Sensor FR 46 System Pressure Behind Pressure Pumps |  |  |  | 421.1W0091 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI27 | 750-455 | 4 |  |  | ACC_SENSOR_1_OUTPX | +CB.2 | 4500 AMCS | 45019001_1 | Acceleration Sensor 1 Output X |  |  |  | 615.2W0003 | [14 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI28 | 750-455 | 1 |  |  | ACC_SENSOR_1_OUTPY | +CB.2 | 4500 AMCS |  | Acceleration Sensor 1 Output Y | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI28 | 750-455 | 2 |  |  | ACC_SENSOR_1_OUTPZ | +CB.2 | 4500 AMCS |  | Acceleration Sensor 1 Output Z | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI28 | 750-455 | 3 |  |  | LEVEL_GREY_WATER_TANK_FWD_SB | +CB.2 | 3400 SEWAGE | 34001025_4 | Level Sensor Grey Water Tank Fwd FR 33 SB |  |  |  | 447W0022 | [14 empty] | 4-20mA
R1.10 |  | Float | KEB2 | AI28 | 750-455 | 4 |  |  | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B05 | +CB.2 | 2500 TECHWATER | 25004037_2 | Flow Sensor Reel For Deckwash B05 |  |  |  | 421.2W0034 | 2x2x0.75 | [13 empty] | 4-20mA
R1.10 |  | Float | KEB2 | AI29 | 750-455 | 1 |  |  | TECH_WAT_FLOW_REEL_FOR_DECKWASH_B06 | +CB.2 | 2500 TECHWATER | 25004037_3 | Flow Sensor Reel For Deckwash B06 |  |  |  | 421.2W0035 | 2x2x0.75 | [13 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI29 | 750-455 | 2 |  |  | Spare_AI29_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI29 | 750-455 | 3 |  |  | Spare_AI29_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI29 | 750-455 | 4 |  |  | Spare_AI29_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.8 |  | Float | KEB2 | AI30 | 750-450 | 1 |  |  | BOW_THRUST_BEARING_TEMP_DE | +CB.2 | 1500 PROPULSION |  | Bow Thrust Motor Bearing Temperature DE | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI30 | 750-450 | 2 |  |  | BOW_THRUST_BEARING_TEMP_NDE | +CB.2 | 1500 PROPULSION |  | Bow Thrust Motor Bearing Temperature NDE | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI30 | 750-450 | 3 |  |  | Spare_AI30_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI30 | 750-450 | 4 |  |  | Spare_AI30_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 1 |  |  | Spare_AI31_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 2 |  |  | Spare_AI31_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 3 |  |  | Spare_AI31_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI31 | 750-450 | 4 |  |  | Spare_AI31_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI32 | 750-450 | 1 |  |  | Spare_AI32_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI32 | 750-450 | 2 |  |  | Spare_AI32_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI32 | 750-450 | 3 |  |  | Spare_AI32_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI32 | 750-450 | 4 |  |  | Spare_AI32_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI33 | 750-450 | 1 |  |  | Spare_AI33_1_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI33 | 750-450 | 2 |  |  | Spare_AI33_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI33 | 750-450 | 3 |  |  | Spare_AI33_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.9 |  | Float | KEB2 | AI33 | 750-450 | 4 |  |  | Spare_AI33_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2 | [18 empty] | 4-20mA
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 1 |  |  | AmcsPlcPowerModule2FuseBlown | +CB.2 | 4500 AMCS |  | AMCS PLC KEB2 Power Module 2 Fuse Blown | [20 empty] | 809 |  |  |  |  | False |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1.8 |  | Bool | KEB2 | F2 | 750-610 | 2 |  |  | AmcsPlcPowerModule2PowerFailure | +CB.2 | 4500 AMCS |  | AMCS PLC KEB2 Power Module 2 Power Failure | [20 empty] | 810 |  |  |  |  | True |  | TS |  | Alarm | Please consult operation manual for more information |  |  |  |  | 1
R1,10 |  | Bool | KEB2 | AO60 | 750-555 | 1 |  |  | BATT_VENT_AFT_PS_SPEED | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD PS Speed |  |  |  | 412.3W0010 | [12 empty] | 0 | 100 | %
R1,10 |  | Bool | KEB2 | AO60 | 750-555 | 2 |  |  | BATT_VENT_FWD_SB_SPEED | +CB.2 | xxxx VENTILATION |  | Battery Ventilation FWD SB Speed |  |  |  | 412.3W0011 | [12 empty] | 0 | 100 | %
R0.1 |  | Bool | KEB2 | AO60 | 750-555 | 3 |  |  | Spare_AO60_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | AO60 | 750-555 | 4 |  |  | Spare_AO60_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.1 |  | Bool | KEB2 | DO60 | 750-1500 | 1 |  |  | BCKUP_GEN_SERV_PUMP_FIELD_RUNN_FDBCK | +CB.2 | 2100 GENERAL SERVICE | 21001003 | Backup General Service Pump Field Running Feedback |  |  |  | 381W0008
R1.0 |  | Bool | KEB2 | DO60 | 750-1500 | 2 |  |  | Spare_DO60_2_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 3 |  |  | Spare_DO60_3_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 4 |  |  | Spare_DO60_4_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 5 |  |  | Spare_DO60_5_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 6 |  |  | Spare_DO60_6_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 7 |  |  | Spare_DO60_7_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 8 |  |  | Spare_DO60_8_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 9 |  |  | Spare_DO60_9_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 10 |  |  | Spare_DO60_10_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 11 |  |  | Spare_DO60_11_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 12 |  |  | Spare_DO60_12_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 13 |  |  | Spare_DO60_13_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 14 |  |  | Spare_DO60_14_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 15 |  |  | Spare_DO60_15_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
R0.2 |  | Bool | KEB2 | DO60 | 750-1500 | 16 |  |  | Spare_DO60_16_ | +CB.2 | SPARE |  | Spare Yard __+CB.2
| True | [11 empty] | Serial Interface - KEC2 Port1
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var1 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var2 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var3 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var4 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var5 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var6 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var7 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var8 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var9 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var10 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var11 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var12 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var13 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var14 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var15 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var16 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var17 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var18 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var19 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var20 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var21 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var22 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var23 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var24 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var25 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var26 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var27 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var28 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var29 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var30 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var31 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var32 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var33 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var34 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var35 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var36 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var37 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var38 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var39 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var40 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var41 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var42 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var43 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var44 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var45 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var46 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var47 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var48 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var49 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P1 | [5 empty] | Serial__Var50 | GUEST_AREA | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC2 Port2
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var1 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var2 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var3 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var4 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var5 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var6 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var7 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var8 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var9 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var10 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var11 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var12 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var13 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var14 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var15 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var16 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var17 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var18 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var19 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var20 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var21 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var22 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var23 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var24 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var25 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var26 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var27 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var28 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var29 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var30 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var31 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var32 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var33 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var34 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var35 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var36 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var37 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var38 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var39 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var40 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var41 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var42 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var43 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var44 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var45 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var46 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var47 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var48 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var49 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P2 | [5 empty] | Serial__Var50 | GUEST_AREA | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC2 Port3
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var1 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var2 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var3 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var4 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var5 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var6 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var7 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var8 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var9 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var10 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var11 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var12 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var13 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var14 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var15 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var16 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var17 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var18 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var19 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var20 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var21 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var22 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var23 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var24 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var25 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var26 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var27 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var28 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var29 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var30 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var31 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var32 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var33 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var34 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var35 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var36 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var37 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var38 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var39 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var40 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var41 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var42 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var43 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var44 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var45 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var46 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var47 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var48 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var49 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P3 | [5 empty] | Serial__Var50 | GUEST_AREA | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC2 Port4
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var1 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var2 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var3 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var4 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var5 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var6 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var7 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var8 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var9 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var10 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var11 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var12 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var13 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var14 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var15 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var16 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var17 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var18 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var19 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var20 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var21 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var22 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var23 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var24 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var25 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var26 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var27 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var28 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var29 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var30 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var31 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var32 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var33 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var34 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var35 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var36 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var37 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var38 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var39 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var40 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var41 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var42 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var43 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var44 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var45 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var46 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var47 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var48 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var49 | GUEST_AREA | SPARE |  | TODO
R0.1 | True |  | KEC2_P4 | [5 empty] | Serial__Var50 | GUEST_AREA | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC3 Port1
R1.9 |  | Bool | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdStatus | +CB.2 | Navigation Lights |  | Hoistable Anchor FWD Status | [8 empty] | 1 | Coil | 0
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | Coil | 1
R1.9 |  | Bool | NavLights |  |  |  |  | True | Starboard_BowStatus | +CB.2 | Navigation Lights |  | Starboard BOW Status | [8 empty] | 1 | Coil | 2
R1.9 |  | Bool | NavLights |  |  |  |  | True | Portside_BowStatus | +CB.2 | Navigation Lights |  | Portside BOW Status | [8 empty] | 1 | Coil | 3
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINStatus | +CB.2 | Navigation Lights |  | Stb. Nav. Spr. (MAIN) Status | [8 empty] | 1 | Coil | 4
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPStatus | +CB.2 | Navigation Lights |  | Stb. Nav. Spr. (BACKUP) Status | [8 empty] | 1 | Coil | 5
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINStatus | +CB.2 | Navigation Lights |  | Pt. Nav. Spr. (MAIN) Status | [8 empty] | 1 | Coil | 6
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPStatus | +CB.2 | Navigation Lights |  | Pt. Nav. Spr. (BACKUP) Status | [8 empty] | 1 | Coil | 7
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_MAINStatus | +CB.2 | Navigation Lights |  | Anchor AFT (MAIN) Status | [8 empty] | 1 | Coil | 8
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPStatus | +CB.2 | Navigation Lights |  | Anchor AFT (BACKUP) Status | [8 empty] | 1 | Coil | 9
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_MAINStatus | +CB.2 | Navigation Lights |  | Steam. Main (MAIN) Status | [8 empty] | 1 | Coil | 10
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_BACKUPStatus | +CB.2 | Navigation Lights |  | Steam. Main (BACKUP) Status | [8 empty] | 1 | Coil | 11
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_MAINStatus | +CB.2 | Navigation Lights |  | Steam. Mizz. (MAIN) Status | [8 empty] | 1 | Coil | 12
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPStatus | +CB.2 | Navigation Lights |  | Steam. Mizz. (BACKUP) Status | [8 empty] | 1 | Coil | 13
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_MAINStatus | +CB.2 | Navigation Lights |  | NUC Stb180° (MAIN) Status | [8 empty] | 1 | Coil | 14
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_BACKUPStatus | +CB.2 | Navigation Lights |  | NUC Stb180° (BACKUP) Status | [8 empty] | 1 | Coil | 15
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_MAINStatus | +CB.2 | Navigation Lights |  | NUC Pt.180° (MAIN) Status | [8 empty] | 1 | Coil | 16
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_BACKUPStatus | +CB.2 | Navigation Lights |  | NUC Pt.180° (BACKUP) Status | [8 empty] | 1 | Coil | 17
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_MAINStatus | +CB.2 | Navigation Lights |  | Sailing Stb.180° (MAIN) Status | [8 empty] | 1 | Coil | 18
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPStatus | +CB.2 | Navigation Lights |  | Sailing Stb.180° (BACKUP) Status | [8 empty] | 1 | Coil | 19
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_MAINStatus | +CB.2 | Navigation Lights |  | Sailing Pt. 180° (MAIN) Status | [8 empty] | 1 | Coil | 20
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPStatus | +CB.2 | Navigation Lights |  | Sailing Pt. 180° (BACKUP) Status | [8 empty] | 1 | Coil | 21
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINStatus | +CB.2 | Navigation Lights |  | NUC & Sailing (MAIN) Status | [8 empty] | 1 | Coil | 22
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPStatus | +CB.2 | Navigation Lights |  | NUC & Sailing (BACKUP) Status | [8 empty] | 1 | Coil | 23
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_MAINStatus | +CB.2 | Navigation Lights |  | Stern (MAIN) Status | [8 empty] | 1 | Coil | 24
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_BACKUPStatus | +CB.2 | Navigation Lights |  | Stern (BACKUP) Status | [8 empty] | 1 | Coil | 25
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | Coil | 26
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | Coil | 27
R1.9 |  | Bool | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdCtrl | +CB.2 | Navigation Lights |  | Hoistable Anchor FWD Control | [8 empty] | 1 | Coil | 300
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | Coil | 301
R1.9 |  | Bool | NavLights |  |  |  |  | True | Starboard_BowCtrl | +CB.2 | Navigation Lights |  | Starboard BOW Control | [8 empty] | 1 | Coil | 302
R1.9 |  | Bool | NavLights |  |  |  |  | True | Portside_BowCtrl | +CB.2 | Navigation Lights |  | Portside BOW Control | [8 empty] | 1 | Coil | 303
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINCtrl | +CB.2 | Navigation Lights |  | Stb. Nav. Spr. (MAIN) Control | [8 empty] | 1 | Coil | 304
R1.9 |  | Bool | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPCtrl | +CB.2 | Navigation Lights |  | Stb. Nav. Spr. (BACKUP) Control | [8 empty] | 1 | Coil | 305
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINCtrl | +CB.2 | Navigation Lights |  | Pt. Nav. Spr. (MAIN) Control | [8 empty] | 1 | Coil | 306
R1.9 |  | Bool | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPCtrl | +CB.2 | Navigation Lights |  | Pt. Nav. Spr. (BACKUP) Control | [8 empty] | 1 | Coil | 307
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_MAINCtrl | +CB.2 | Navigation Lights |  | Anchor AFT (MAIN) Control | [8 empty] | 1 | Coil | 308
R1.9 |  | Bool | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPCtrl | +CB.2 | Navigation Lights |  | Anchor AFT (BACKUP) Control | [8 empty] | 1 | Coil | 309
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_MAINCtrl | +CB.2 | Navigation Lights |  | Steam. Main (MAIN) Control | [8 empty] | 1 | Coil | 310
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Main_BACKUPCtrl | +CB.2 | Navigation Lights |  | Steam. Main (BACKUP) Control | [8 empty] | 1 | Coil | 311
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_MAINCtrl | +CB.2 | Navigation Lights |  | Steam. Mizz. (MAIN) Control | [8 empty] | 1 | Coil | 312
R1.9 |  | Bool | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPCtrl | +CB.2 | Navigation Lights |  | Steam. Mizz. (BACKUP) Control | [8 empty] | 1 | Coil | 313
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_MAINCtrl | +CB.2 | Navigation Lights |  | NUC Stb180° (MAIN) Control | [8 empty] | 1 | Coil | 314
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_SB180_BACKUPCtrl | +CB.2 | Navigation Lights |  | NUC Stb180° (BACKUP) Control | [8 empty] | 1 | Coil | 315
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_MAINCtrl | +CB.2 | Navigation Lights |  | NUC Pt.180° (MAIN) Control | [8 empty] | 1 | Coil | 316
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_PS180_BACKUPCtrl | +CB.2 | Navigation Lights |  | NUC Pt.180° (BACKUP) Control | [8 empty] | 1 | Coil | 317
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_MAINCtrl | +CB.2 | Navigation Lights |  | Sailing Stb.180° (MAIN) Control | [8 empty] | 1 | Coil | 318
R1.9 |  | Bool | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPCtrl | +CB.2 | Navigation Lights |  | Sailing Stb.180° (BACKUP) Control | [8 empty] | 1 | Coil | 319
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_MAINCtrl | +CB.2 | Navigation Lights |  | Sailing Pt. 180° (MAIN) Control | [8 empty] | 1 | Coil | 320
R1.10 |  | Bool | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPCtrl | +CB.2 | Navigation Lights |  | Sailing Pt. 180° (BACKUP) Control | [8 empty] | 1 | Coil | 321
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINCtrl | +CB.2 | Navigation Lights |  | NUC & Sailing (MAIN) Control | [8 empty] | 1 | Coil | 322
R1.9 |  | Bool | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPCtrl | +CB.2 | Navigation Lights |  | NUC & Sailing (BACKUP) Control | [8 empty] | 1 | Coil | 323
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_MAINCtrl | +CB.2 | Navigation Lights |  | Stern (MAIN) Control | [8 empty] | 1 | Coil | 324
R1.9 |  | Bool | NavLights |  |  |  |  | True | Stern_BACKUPCtrl | +CB.2 | Navigation Lights |  | Stern (BACKUP) Control | [8 empty] | 1 | Coil | 325
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | Coil | 326
R1.9 | True | Bool | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | Coil | 327
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerMainOn | +CB.2 | Navigation Lights |  | PowerMainOn | [8 empty] | 1 | Coil | 1000
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerEmergencyOn | +CB.2 | Navigation Lights |  | PowerEmergencyOn | [8 empty] | 1 | Coil | 1001
R1.9 |  | Bool | NavLights |  |  |  |  | True | PowerLampsOn | +CB.2 | Navigation Lights |  | PowerLampsOn | [8 empty] | 1 | Coil | 1002
R1.9 |  | Bool | NavLights |  |  |  |  | True | ManualOperationActive | +CB.2 | Navigation Lights |  | ManualOperationActive | [8 empty] | 1 | Coil | 1003
R1.9 |  | Bool | NavLights |  |  |  |  | True | CommunicationError | +CB.2 | Navigation Lights |  | CommunicationError | [8 empty] | 1 | Coil | 2000
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Hoistable_Anchor_FwdOpTime | +CB.2 | Navigation Lights |  | Hoistable Anchor FWD Operating Time | [8 empty] | 1 | HoldingRegister | 40000 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | HoldingRegister | 40002 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Starboard_BowOpTime | +CB.2 | Navigation Lights |  | Starboard BOW Operating Time | [8 empty] | 1 | HoldingRegister | 40004 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Portside_BowOpTime | +CB.2 | Navigation Lights |  | Portside BOW Operating Time | [8 empty] | 1 | HoldingRegister | 40006 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | SB_Nav_Spr_MAINOpTime | +CB.2 | Navigation Lights |  | Stb. Nav. Spr. (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40008 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | SB_Nav_Spr_BACKUPOpTime | +CB.2 | Navigation Lights |  | Stb. Nav. Spr. (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40010 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | PS_Nav_Spr_MAINOpTime | +CB.2 | Navigation Lights |  | Pt. Nav. Spr. (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40012 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | PS_Nav_Spr_BACKUPOpTime | +CB.2 | Navigation Lights |  | Pt. Nav. Spr. (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40014 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Anchor_Aft_MAINOpTime | +CB.2 | Navigation Lights |  | Anchor AFT (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40016 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Anchor_Aft_BACKUPOpTime | +CB.2 | Navigation Lights |  | Anchor AFT (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40018 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Main_MAINOpTime | +CB.2 | Navigation Lights |  | Steam. Main (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40020 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Main_BACKUPOpTime | +CB.2 | Navigation Lights |  | Steam. Main (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40022 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Mizz_MAINOpTime | +CB.2 | Navigation Lights |  | Steam. Mizz. (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40024 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Steam_Mizz_BACKUPOpTime | +CB.2 | Navigation Lights |  | Steam. Mizz. (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40026 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_SB180_MAINOpTime | +CB.2 | Navigation Lights |  | NUC Stb180° (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40028 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_SB180_BACKUPOpTime | +CB.2 | Navigation Lights |  | NUC Stb180° (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40030 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_PS180_MAINOpTime | +CB.2 | Navigation Lights |  | NUC Pt.180° (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40032 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_PS180_BACKUPOpTime | +CB.2 | Navigation Lights |  | NUC Pt.180° (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40034 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_SB180_MAINOpTime | +CB.2 | Navigation Lights |  | Sailing Stb.180° (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40036 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_SB180_BACKUPOpTime | +CB.2 | Navigation Lights |  | Sailing Stb.180° (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40038 | [7 empty] | Minutes
R1.10 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_PS180_MAINOpTime | +CB.2 | Navigation Lights |  | Sailing Pt. 180° (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40040 | [7 empty] | Minutes
R1.10 |  | Uint32 | NavLights |  |  |  |  | True | Sailing_PS180_BACKUPOpTime | +CB.2 | Navigation Lights |  | Sailing Pt. 180° (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40042 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_and_Sailing_MAINOpTime | +CB.2 | Navigation Lights |  | NUC & Sailing (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40044 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | NUC_and_Sailing_BACKUPOpTime | +CB.2 | Navigation Lights |  | NUC & Sailing (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40046 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Stern_MAINOpTime | +CB.2 | Navigation Lights |  | Stern (MAIN) Operating Time | [8 empty] | 1 | HoldingRegister | 40048 | [7 empty] | Minutes
R1.9 |  | Uint32 | NavLights |  |  |  |  | True | Stern_BACKUPOpTime | +CB.2 | Navigation Lights |  | Stern (BACKUP) Operating Time | [8 empty] | 1 | HoldingRegister | 40050 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | HoldingRegister | 40052 | [7 empty] | Minutes
R1.9 | True | Uint32 | NavLights |  |  |  |  | True | SPARE | +CB.2 | Navigation Lights |  | SPARE | [8 empty] | 1 | HoldingRegister | 40054 | [7 empty] | Minutes
| True | [11 empty] | Serial Interface - KEC3 Port2
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var1 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var2 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var3 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var4 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var5 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var6 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var7 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var8 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var9 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var10 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var11 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var12 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var13 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var14 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var15 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var16 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var17 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var18 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var19 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var20 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var21 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var22 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var23 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var24 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var25 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var26 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var27 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var28 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var29 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var30 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var31 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var32 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var33 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var34 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var35 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var36 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var37 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var38 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var39 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var40 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var41 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var42 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var43 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var44 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var45 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var46 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var47 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var48 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var49 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P2 | [5 empty] | Serial__Var50 | +CB.2 | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC3 Port3
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var1 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var2 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var3 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var4 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var5 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var6 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var7 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var8 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var9 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var10 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var11 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var12 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var13 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var14 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var15 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var16 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var17 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var18 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var19 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var20 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var21 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var22 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var23 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var24 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var25 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var26 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var27 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var28 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var29 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var30 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var31 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var32 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var33 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var34 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var35 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var36 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var37 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var38 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var39 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var40 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var41 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var42 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var43 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var44 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var45 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var46 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var47 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var48 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var49 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P3 | [5 empty] | Serial__Var50 | +CB.2 | SPARE |  | TODO
| True | [11 empty] | Serial Interface - KEC3 Port4
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var1 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var2 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var3 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var4 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var5 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var6 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var7 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var8 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var9 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var10 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var11 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var12 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var13 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var14 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var15 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var16 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var17 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var18 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var19 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var20 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var21 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var22 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var23 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var24 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var25 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var26 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var27 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var28 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var29 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var30 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var31 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var32 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var33 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var34 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var35 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var36 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var37 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var38 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var39 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var40 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var41 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var42 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var43 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var44 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var45 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var46 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var47 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var48 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var49 | +CB.2 | SPARE |  | TODO
R0.1 | True |  | KEC3_P4 | [5 empty] | Serial__Var50 | +CB.2 | SPARE |  | TODO
| True | [11 empty] | EOF

## Help
IO list format
The Chameleon automation system can automatically read an I/O list, but it requires a fixed format. If the customer insists on different column names, we can use alias names which have to be defined custom in the software. The default format of the list:
Mandatory [1] | Name (key) |  | Description | Omschrijving
Yes | Acknowledge location |  | Location where alarm can be acknowledged. This can only be one single location, the location name can be chosen as you wish, but keep in mind to use abbreviations and use it consistently in the IO list. This will be solved by using a pull down list to choose from. | Locatie waar het alarm geaccepteerd kan worden. Dit mag slechts 1 enkele locatie zijn, de naam van de locatie is vrij te kiezen, meestal gebruiken we afkortingen. Let er wel op dat de locatie consequent juist in de lijst wordt ingevuld. Dit zal worden afgedwongen met een pull down lijst.
|  |  | For example: | Enkele voorbeelden;
|  |  | - Wheelhouse: “WH” | - Wheelhouse: “WH”
|  |  | - Engine control room: “ECR” | - Engine control room: “ECR”
|  |  | - Engine room PS: “ERPS” | - Engine room PS: “ERPS”
|  |  | - Tech space below WH: “TSBWH” | - Tech space below WH: “TSBWH”
Yes | Alarm level | HH | High-high condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “1100”. Alarm becomes active if signal > 1100 | Hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 1100. Alarm (HH) wordt dan actief bij waarde > 1100
Yes |  | H | High condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “1000”. Alarm becomes active if signal > 1000 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 1000. Alarm (H) wordt dan actief bij waarde > 1000
Yes |  | L | Low condition setpoint (value in units of signal). Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “600”. Alarm becomes active if signal < 600 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 600. Alarm (H) wordt dan actief bij waarde < 600
Yes |  | LL | Low-low condition setpoint (value in units of signal Only for analog alarms, just provide a value within the range of column [range lower] and [range upper], e.g. “500”. Alarm becomes active if signal < 500 | Hoog-hoog conditie setpoint (signaal waarde). Alleen voor analoge alarmen, vul hier een waarde in binnen de range gedefinieerd binnen de waarden in de kolommen [Range lower] en [Range upper], b.v. 500. Alarm (H) wordt dan actief bij waarde < 500
Yes |  | F | Setpoint for fault condition of binary I/O: “True” (for active) or “False” (for inactive). Therefore whetthe setpoint is "False" and the actual signal becomes inactive, the alarm will become active after the on delay time [Delay on] | Setpoint voor fout conditie van binaire I/O: "True" (voor actief) en "False" (voor inactief). Dus als setpoint is "False" en het signaal wordt inactief (NC), dan gaat wordt het alarm actief na het verstrijken van de off delay [Delay on]
Yes | Alert Code |  | Unique alert code, not as key for this list, but mandatory for a alarm definition | Deze unieke alert code is ontstaan om ondubbelzinnig over een alarm te kunnen communiceren en is alleen verplicht voor alarmen.
No | Cabinet |  | Cabinet number or name for selection filtering, not mandatory, therefore the syntax will not be checked. (This text will also be displayed in I/O list on screen) | Cabinet naam of nummer is hier in te vullen, deze gegevens kunnen voor selectiefilters worden gebruikt en wordt vermeld in het I/O lijst, maar er is geen invulverplichting.
No | Cable Core No |  | Core number isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Core No. (ader nummer) is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Cable ID |  | Cable id isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Cable ID is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Cable Type |  | Cable type isn’t mandatory and only for convenience, therefore the syntax will not be checked. | Cable Type is niet verplicht om in te vullen, wordt wel weergegeven in I/O lijst
No | Call GEA on Alert |  | Automatically trigger a GEA when this alert becomes active | Veroorzaak een GEA als dit alarm actief wordt
Yes | Data Type |  | Type of data, Valid data types are: | Date type, valide types zijn:
|  |  | - Boolean: “Bool” | - Booleon: "Bool"
|  |  | - 16 bits word: “Word16” | - 16 bits word: “Word16”
|  |  | - Signed 16 bits integer: “Int16” | - Signed 16 bits integer: “Int16”
|  |  | - Unsigned 16 bits integer: “UInt16” | - Unsigned 16 bits integer: “UInt16”
|  |  | - Signed 32 bits integer: “Int32” | - Signed 32 bits integer: “Int32”
|  |  | - Unsigned 32 bits integer: “UInt32” | - Unsigned 32 bits integer: “UInt32”
|  |  | - Signed 64 bits integer: “Int64” | - Signed 64 bits integer: “Int64”
|  |  | - Floating point number: “Float” | - Floating point number: “Float”
|  |  | - Date and time: “DateTime” | - Date and time: “DateTime”
|  |  | - String of ASCII chars: “AsciiString(N)” (where N is the number of characters in the string.) | - String van ASCII chars: “AsciiString(N)” (N is het aantal karakters in de string.)
|  |  | DateTime should be a 32-bit word that counts the number of seconds since 1970-01-01T00:00:00Z. | DateTime moet een 32--bit word zijn de het aantal seconden telt vanaf 1970-01-01T00:00:00Z
|  |  | Hardwired DI and DO type signals are Bool; AI and AO are UInt16 | Bekabelde DI en DO signalen zijn van het type Boolean, AI en AO zijn Uint16
Yes | Delay On |  | Delay time for activating the alert, e.g. for 4 seconds delay: “4” | Inschakel vertraging voor het alarm in seconden, b.v. 4 sec vertraging: "4"
Yes | Deleted |  | Row has been deleted and should be ignored (mark with revision letter when row was deleted). | Deze rij is verwijderd en wordt genegeerd, maar blijft staan vanwege revisiebeheer of het is van tijdelijke aard.
Yes | Description |  | Description of signal, this tekst is also used as an alarm description, e.g. "Common alarm valve system" | Beschrijving van het signaal, deze tekst wordt ook gebruikt als alarmtext, e.g. "Algemeen alarm kleppen besturing"
Yes | Device |  | Unique identifier for device providing the IO. For example; | De unieke devicenaam waar het item bij hoort, bijvoorbeeld;
|  |  | - Hardwired:: PLC OID -> "70UP100" | - Bedraad: PLC OID -> "70UP100"
|  |  | - Serial with gateway (MB/RTU -> MB/TCP): Gateway OID -> "GW1" | - Serieel middels een gateway (MB/RTU -> MB/TCP): Gateway OID -> "GW1"
|  |  | - Serial directly to PLC comm. Kaart: PLC OID -> "70UP100" | - Serieel middels een PLC comm. Kaart: PLC OID -> "70UP100"
|  |  | - Modbus TCP/IP: MB-device OID -> "MainEngine" | - Modbus TCP/IP: MB-device OID -> "MainEngine"
Yes | Disallow Inhibit |  | Do not allow alert to be inhibited, when marked with an “X” | Sta niet toe dat dit item ge-inhibit kan worden. Gebruik bij voorkeur een "X" om aan te geven dat deze optie actief is.
No | Do Not Export |  | When not empty, item will not be exported into Codesys export files for wago | Als dit veld niet leeg is, zal dit item niet worden meegenomen in de export files voor codesys, dit veld is voorlopig specifiek voor wago plc's
No | Do Not Log |  | When not empty, item will not be logged when using datalogging | Als dit veld niet leeg is, zal dit item niet worden meegenomen in de datalogging,
No | Log to Daily Report |  | Include this I/O in the engine room report | Gebruik dit I/O in het engine room report.
Yes | General Lock[3] Tag | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | Group Alarm |  | Resound alert if input is toggled, despite being silenced. If the alarm signal is meant as a common or groupalarm, this alert can be setup to resound the it alarm horn then alarmlevel is toggled. | Opnieuw de alarm hoorn activeren als de alarm ingang opnieuw geactiveerd wordt, ondankt dat de hoorn voor dit alarm is afgezet. Als het item bedoeld is als een groepsalarm, dan kan dit alart worden ingesteld als groupsalarm, waardoor de hoorn opnieuw kan afgaan bij verandering van de ingang.
Yes | H Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | HH Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | I/O type |  | Type of I/O: | I/O type:
|  |  | - Digital input: “DI” | - Digitale input: "DI"
|  |  | - Digital output: “DO” | - Digitale output: "DI"
|  |  | - Analog input (also PT100): “AI” | - Analoge input: "AI"
|  |  | - Analog output: “AO” | - Analoge output: "AO"
|  |  | - Serial io: “SE” | - Seriële I/O: "SE"
Yes | Intended Operator Response |  | Field to provide extra information and to provide some pointers about the cause and probable solutions to fix the cause of this alert. This is a new mandatory column expected by class. For now class expects as a minimal effort to direct the operator to the operator manual. | Dit veld is bedoeld om extra informate en tips te geven omtrend dit alarm (b.v. een samenvatting uit de handleiding zijn) om de alarm situatie adequaat op te kunnen lossen. Dit is een relatief nieuwe kolom waarbij klasse in eerste in stantie minimaal een verwijzing naar het handboek verwacht.
Yes | L Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | LL Lock | Tag | Syntax [Device].[Tag] of I/O signal that locks the alarm as lock as the lock conditions are met | Syntax [Device].[Tag] van I/O die het lock signaal is voor dit alarm. Locken van een alarm is onderdrukken van het alarm zolang aan de lock voorwaarde voldaan wordt.
Yes |  | Operator | How to compare the lock signal to the lock level setpoint, for instance; | Welke vergelijking op de waarde van het signaal is nodig om het alarm te locken, bijvoorbeeld;
|  |  | - analog signaal > <waarde> (greater dan) -> operator ">" | - analoog signaal > <waarde> (groter dan) -> operator ">"
|  |  | - analog signal < <waarde> (less than) -> operator "<" | - analoog signaal < <waarde> (kleiner dan) -> operator "<"
|  |  | - digital signal equal to actief (= 1) -> operator "=" | - digitaal signaal gelijk aan actief (= 1) -> operator "="
|  |  | Valid operators are, digital signal: "=" (equal), analog signal "<" (less than) or ">" (greater than) | Valide operators zijn digitaal signaal : "=" (gelijk aan), analoog signaal : "<" (kleiner dan) of ">" (groter dan)
Yes |  | Level | Level setpoint to compare to lock signal. | Niveau voor de vergelijking met de huidige waarde.
|  |  | For digital signals: “0” or “1” | -Digitaal signaal: "0" (voor inactief) of "1" (voor actief)
|  |  | For analog values: anything within the already defined range in columns Range upper and lower | -analoog signaal: Elke waarde binnen de range in kolommen [Range upper] en [Range lower]
Yes | Modbus address |  | Modbus address for the I/O (format <word address>.<bit nr> or <bit address> in decimals) | Modbus address voor de I/O in het volgende formaat <word address>.<bit nr> or <bitaddress> allen in decimalen
Yes | Modbus function codes |  | Allowed Modbus functions at this Modbus address. Separate by comma when multiple codes are allowed. (Modbus protocol only) for modbus codes. | Modbus function code voor dit address, Als er meerdere functiecodes zijn toegestaan dan kun je die hier gescheiden door komma's invullen
Yes | Modbus slave address |  | Modbus slave address for external device. Mandatory for modbus signals | Modbus slave adres voor devices die via modbus communiceren, in dat geval it het een verplicht veld
Yes | Module |  | Device module where the IO is connected (not used for serial interface that are not connected to a [Device]) [2]. | Device module waarop het item is aangesloten. In het geval van een PLC bedoelen we de I/O kaart OID -> "DI1", deze kolom wordt niet gebruikt bij seriële signalen.
|  |  | For example: | Bijvoorbeeld:
|  |  | - The first Digital input card: “DI1” | - De eerst digitale ingangskaart: "DI1"
|  |  | - The second analog output card: “AO2” | - De tweede analoge outgangskaart: "AO2"
|  |  | - Can also be used to indicate switch OID for TCP/IP signals, e.g. "7U2" | - Kan bij TCP-IP verbindingen worden gebruikt om het switch OID aan te geven, b.v. "7U2"
Yes | OPC UA | Node ID | The unique identifier for a node in an OPC server’s address space | Het unique id voor de node dat bij dit signaal hoort in een OPC server zijn address space
Yes | OPC UA | Publish Interval | The publishi interval (in ms) is the cycle time at which a subscription executes | De publish interval is de tijd wanneer een subscription wordt uitgevoerd
No | P&ID |  | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht | No | P&ID | P & ID names for cross-references isn’t mandatory and only for convenience, therefore the syntax will not be checked. | P & ID names voor referenties op tekeningen staan voor weergave in de lijst, invullen is dus niet verplicht
Yes | Priority |  | Alarm priority type: “alarm”, “emergency”, “warning”, “caution” or empty (if unsure, use “alarm”), mandatory if item is an alarm. | Alarm prioriteit, we onderscheiden de volgende types: “alarm”, “emergency”, “warning”, “caution” of leeg laten bij geen alarm (als je het niet zeker weet, neem dan standaard “alarm”. Deze kolom is verplicht voor alarmen.
Yes | Range | Lower | Lower value of range. (Mandatory for analog signals) | Laagste waarde van de school (verplicht voor analoge signalen)
Yes |  | Upper | Upper value of range. (Mandatory for analog signals) | Hoogste waarde van de school (verplicht voor analoge signalen)
Yes | Rev |  | Last revision when the row has changed. | Revisie van de laatste wijziging
Yes | Sounding Locations |  | Additional locations where alarm buzzer should be activated, using the same location names as the acknowledge location, e.g. “WH,ECR,ERPS”. This option doen's affect the way alarms are displayed, all alarms are displayed on every workstation, bus by using samrt sorting techniques, sorting is based upon location, alert priority and timestamp. Alarms from other locations can be found further down the active alarm list or on top if there are no alarms for this location. | Additionele locaties waar de alarm hoorn ook af moet gaan als het alarm actief word, hierbij worden dezelfde locatie namen gebruikt als bij de kolom [Acknowledge location], locaties worden dan door komma's geschieden, b.v.; "WH,ECR,ERPS". Deze optie heeft niets te maken met het tonen van alarmen. Alle alarmen worden op alle workstations getoond, maar door slimme sorteermethodes worden de alarmen gesorteerd wordt op locatie, alert prioriteit en tijdsstempel.
Yes | System |  | Used for sorting by system, when using this column, system grouping can be used, for instance in the I/O maintenance screen. Intended to be a short description e.g. "ME PS" or "FAS" or "TMS". Max 16 characters. | Wordt gebruikt voor het sorteren van de items, bijvoorbeeld in het I/O lijst scherm onder maintenance. Bedoeld als korte omschrijving, bijv. "ME PS" of "FAS" of "TMS". Max 16 karacters.
Yes | Tag |  | Unique IO identifier (Composed of an SFI code and an abbreviation for the function) | Uniek id voor dit signaal, dit mag een SFI codering zijn of in de meeste gevallen iets beschrijvends, zoals "CommonAlarm"
Yes | Is Subscribe |  | Define if the line is a subscribe to another Tag in the I/O List. | Specificeert of the lijn “subscribed” op een andere lijn in de I/O lijst
Yes | Prefix Device |  | The tag will be published in our system with the device as a prefix | De tag wordt gepubliseerd met de devicenaam als voorvoegsel in ons systeem
Yes | Terminal |  | To further specify the signals connected to the [Module], use the input number of the i/o module mentioned in column [Module], e.g. third input on DI: “3” | Deze kolom is bedoeld ter aanvulling van de kolom [Module], hier geef je aan op welke in- of uitgang van de [Module] het signaal is aangesloten, b.v. derde input op DI2: "3"
|  |  | For serial interfaces: | Voor seriële interfaces:
|  |  | - With gateway: Port number on gateway e.g. "2" | - Bij gebruik van een Gateway: Poortnummer op gateway, b.v. "2"
|  |  | - Directly to PLC: not used | - Direct op een [Device] zonder module, b.v. "X2"
|  |  | - Modbus TCP/IP: Port number on switch, e.g. "3" | - Kan bij TCP/IP verbindingen worden gebruikt voor poortnummer op switch, b.v. "1"
No | Timestamp |  | Workstation of last change in io item | Geeft aan op welk werkstation de laatste wijziging is gedaan
Yes | Unit |  | Unit of the measured value. For example; Bar, mA | Eenheid van het te meten signaal. Bijvoorbeeld Bar, mA, wordt o.a. gebruikt voor trending
Yes | VDR ID |  | Send all changes to voyage data recorder. Mark with unique ID number, which will also be send to the VDR system. Leaving the column empty means, VDR notification is not applicable | Middels deze kolom is aan te geven of het alarm doorgezet moet worden naar het VDR systeem, waar van toepassing. Als deze kolom niet leeg is, is het doorsturen van toepassing. Gebruik bij voorkeur een unit id nummer welke meegezonden wordt naar de VDR.
No | Workstation |  | Do not used, colums is used by system to indicate workstation of last change in io item | Niet gebruiken, deze kolom wordt door het systeem gebruikt om aan te geven op welk werkstation de laatste wijziging is gedaan
No | Yard Tag |  | Informative item for separated Yard id numbering or e.g. for SFI coding | Informatief veld voor b.v. aparte werfcondering of SFI codering.
Additional columns are allowed, if the column is not defined in the list above, it will be ignored. Examples are; - Green line (level for green line on gauge to indicate nominal value) - Red line (for max level) - Specific ID's - Extended cabinet name / location - Eplan coding - Prefix - etc. |  |  |  | Meer kolommen toevoegen voor meer detailering / extra informatie of kruisverwijzingen is geen probleem, onbekende kolommen worden genegeerd. Bijvoorbeeld; - Green line (nominale niveau die met een groene lijn op een meter wordt aangegeven) - Red line (max niveau die je aan aangeven met een rode lijn) - Kruisverwijzingen / ID's - Uitgebreidere omschrijvingen van panelen en locaties - Prefix - etc.
[1] Mandatory columns can be empty, but they have to be defined in the I/O list

## Internal lists
Direction | Data Type | Alert Priority | Lock Operator | True False | Modbus Data Type | Module Type
In | Bool | Emergency | < | True | Coil | ReadFieldbus
InOut | Int16 | Alarm | > | False | Input | WriteFieldbus
Out | Int32 | Warning | = |  | InputRegister | ReadWriteFieldbus
| Int64 | Caution |  |  | HoldingRegister | RetainPersistent
| UInt16 | Event |  |  |  | Other
| UInt32 |  |  |  |  | 750-403
| UInt64 |  |  |  |  | 750-430
| Float |  |  |  |  | 750-454
| Double |  |  |  |  | 750-455
| DateTime |  |  |  |  | 750-461
| TimeSpan |  |  |  |  | 750-461/000-003
| UnixDateTime |  |  |  |  | 750-464#02-RTD-PT
| String |  |  |  |  | 750-485
| AsciiString |  |  |  |  | 750-511/000-001
| IpAddress |  |  |  |  | 750-511/000-002
| Blob |  |  |  |  | 750-517
750-530
750-554
750-555
750-610
750-1400
750-1415
750-1425
750-1500
750-1515