# Hull temperature sensors

See drawing: 3094-45-016 for sensor positions

## Hardware

|  | PT100 Pos: 94455001 Type: DLE124A |
| --- | --- |
|  | HART Temperature transmitter 1ch Pos: 94455002 PR Electronics 5437A-1-M |
|  | HART Temperature transmitter 2ch Pos: 94455003 PR Electronics 5437A-2-M |
|  | HART Ethernet gateway |

## Transmitter connect

Connect PT100:

Connect loop link:

Note: only connect transmitters parallel when configured with a unique polling address. 
default polling address is 0.

Note: When only programming the transmitter no external 24V required, only connect the red and black wire.

Note: When transmitter is connected with more than 2 devices parallel it is not possible to program the device with the loop link.

Gateway connection:

## Transmitter configuration

Each transmitter must have an unique polling address with a value from 0..63
Use the tool Preset to configure the transmitter.

Configuration tool:
https://www.prelectronics.com/downloads/software/preset-software/

Set polling range to be able to connect all transmitters:  
Tools->Options: 

Press receive to detect connected transmitters.

Once connected change the configuration. 
Or use the configuration file: 94455002_xx.cfg or 94455003_xx.cfg and only change polling address and tag number.

| Tab | Settings |
| --- | --- |
| Input 1 |  |
| Input 2 | For 537A1 For 537A2 |
| Device Variables | For 537A1 For 537A2 |
| Output analog output signal not used, set to max 4mA and disable wire break detection. |  |
| HART: protocol: HART7 Tag: Vitters sub number see table Long Tag: Vitters part number see table Polling address: see table Output current: 4mA for each transmitter even with Loop Current Mode disable. |  |

## HES Gateway configuration

Tools: PACTware

Backup in configuration file: 3094_HES_Configuration.PW5

## HART Channels

Configure the HART input channels by adding the polling addresses of the corresponding loop.

Each device should be configured as Command 3: (is default)

## Modbus settings

64 device variables can be mapped to modus registers. 
Loop 1: DV1-16, Loop 2: DV17-32, Loop 3: DV33-48, Loop 4: DV49-64
For transmitter ch1 choose PV and for ch2 SV

## IP Address
To change the IP address use the tool “NAC Client”

## Data format

IEEE 754 Floating Point values 32-bit
One value data is available in two modbus registers.

Modbus data:

C# Conversion example:

var data = new byte[] { 0xE6, 0xD4, 0x9D, 0x41 }; var value = BitConverter.ToSingle(data, 0); Console.WriteLine($"Value is {value}");

Output: Value is 19,728954

Value >850°C is sensor failure.
Value NaN is transmitter disconnected / HART Communication failure.